# (AKRSP)

# STANDARD BIDDING DOCUMENTS

# FOR

# SUPPLY, INSTALLATION, COMMISSIONING AND TEST RUNNING

# OF

# TURBINE-GENERATOR UNIT

# FOR

# 230 KW DIZG HYDRO POWER PROJECT

# KHUSHAL CLUSTER DIZG—YARKHOON VALLEY DISTRICT UPPER CHITRAL

# NOVEMBER 2025

INVITATION

FOR

BIDS

INVITATION FOR BIDS

Date: ______________

Bid Reference No.: Dizg 6.1.1.2.3

- The Aga Khan Rural Support Programme (AKRSP) is implementing Th project Energy Plus  Energy Plus: Energy for Climate Resilience in Gilgit-Baltistan (GB) and Upper/Lower Chitral districts in Khyber Pakhtunkhwa (KP) The Energy Plus  Access to Clean Energy in Northern Pakistan programme, led by the Aga Khan Foundation with funding from the European Union, aims to provide clean, reliable, and affordable energy to over 350,000 people in Gilgit-Baltistan and Chitral, regions with limited access to the national grid. The initiative focuses on three key outcomes: enabling renewable energy transition through new generation capacity, improved transmission, and green economic opportunities; enhancing natural resource management by protecting ecosystems and planting over 2.5 million trees; and strengthening sustainable development by promoting energy efficiency in public buildings, supporting small enterprises, and engaging civil society in policy and planning. Designed to be climate-resilient and low carbon, the programme supports Pakistan’s commitments under the Paris Agreement while reducing reliance on traditional biomass fuels.

(the “Employer”) has undertaken the rehabilitation of a Hydropower Project in Brep Cluster and it is intended that part of the allocated funds will be applied to eligible payments under the Contract titled “Rehabilitation and Upgradation of 230KW Dizg Hydropower Project at Yukum, Yarkhoon Valley District Upper Chitral”, and it is intended that part of the allocated funds will be applied to eligible payments under the Contract for “Supply, Installation, Commissioning & Testing Running of Turbine- Generator Unit”.

- The Employer invites sealed bids from eligible Firms or Contractors on Single Stage - two Envelope, bidding procedure.

- The Bidders may obtain any information concerning the bids through email, or inspect personally at, and acquire the Bidding Documents or get the soft copy through the following email addresses:

procurement_akrsppk@akdn.org

With copy to:

- Mr. Mir Alam, through e-mail: mir.alam@akdn.org

- All bids must be accompanied by a Bid Security to the amount of 2%, of the Bid value, and shall be, in the form of Deposit at Call, from any scheduled bank in Pakistan or from a foreign bank duly counter guaranteed by a scheduled bank in Pakistan, in favor of the employer, valid for a period of 28 days beyond the bid validity date. The bid security must be in separate sealed envelope and clearly written bid security with technical bid.

- A complete set of Bidding Documents may be downloaded from AKRSP web page by an interested bidder, and payment of a non-refundable fee of Rs. 5000/- (Rupees three Thousand Only) must be submitted in technical bid through bank draft in the name of AKRSP.

- Bids must be delivered to the Office of the Employer, at AKRSP, Head Office at Gilgit, Phone No. 05811-45034/452679 at or before December 8th, 2025 at 17:00 hours, Pakistan standard time.  Late Bids will be rejected.

- Bidders shall have the option of submitting their Bids electronically (scanned copies) to the email addresses procurement_akrsppk@akdn.org with copy to mir.alam@akdn.org. The instruction for electronic submission is provided in IB 18.6.

- Bids will be opened at 15:30 hours on 10th December 2025 (or any change in the opening date, will be informed to prospective bidders a day before the above given date), in the presence of bidders’ representatives who choose to attend.

Head Administration

AKRSP, Core Office, Gilgit

INSTRUCTIONS

TO

BIDDERS

TABLE OF CONTENTS

# INSTRUCTIONS TO BIDDERS

## Clause no	Description

# A. GENERAL

IB.1	Scope of Bid and Source of Funds

IB.2	Eligible Bidders

IB.3	Eligible Goods and Services

IB.4	Cost of Bidding

B. BIDDING DOCUMENTS

IB.5	Contents of Bidding Documents

IB.6	Clarification of Bidding Documents

IB.7	Amendment of Bidding Documents

C. PREPARATION OF BIDS

IB.8	Language of Bid

IB.9	Documents Comprising the Bid

IB.10	Form of Bid and Schedules

IB.11	Bid Prices

IB.12	Currencies of Bid

IB.13	Documents Establishing Bidder’s	
	Eligibility and Qualification

IB.14	Documents Establishing Good’s Eligibility	
	and Conformity to Bidding Documents

IB.15	Bid Security

IB.16	Validity of Bids

IB.17	Format and Signing of Bid

D. SUBMISSION OF BIDS

IB.18	Sealing and Marking of Bids

IB.19	Deadline for Submission of Bids

IB.20	Late Bids

IB.21	Modification, Substitution and Withdrawal of Bids

E.BID OPENING AND EVALUATION

IB.22	Bid Opening

IB.23	Clarification of Bids

IB.24	Preliminary Examination & Determination of

Responsiveness of Bids

IB.25	Conversion to Single Currency

IB.26	Detailed Evaluation of Bids

IB.27	Process to be Confidential

F. AWARD OF CONTRACT

IB.28	Post-Qualification

IB.29	Award Criteria

IB.30	Employer’s Right to Vary Quantities

IB.31	Employer’s Right to Accept any Bid and to

Reject any or all Bids

IB.32	Notification of Award

IB.33	Performance Security

IB.34	Signing of Contract Agreement

G. ADDITIONAL INSTRUCTIONS

IB.35	Instructions not Part of Contract

IB.36	Contract Documents

IB.37	Sufficiency of Bid

IB.38	One Bid per Bidder

IB.39	Bidder to Inform Himself

IB.40	Alternate Proposals by Bidder

IB.41	Local Conditions

IB.42	Integrity Pact

# H. APPENDICES

–	Appendix A to Instructions to Bidders:

Name of Eligible Countries

–	Appendix B to Instructions to Bidders:

Evidence of Bidder’s Capability

–	Appendix C to Instructions to Bidders:

Domestic Goods (value added in Pakistan)

INSTRUCTIONS TO BIDDERS

A. 	GENERAL

IB.1 	Scope of Bid and Source of Funds

  - Scope of Bid

Aga Khan Rural Supports Programme (AKRSP) hereinafter called “the Employer” intends to receive bids for the work: “Supply, installation, commissioning and test running of Turbo Generating Unit for 230 kW Dizg Hydro Power Project at village Yukum, Yarkhoon valley District Upper Chitral” The parameters are as detailed below.

The complete scope of bid includes, trash racks, penstock pipe including the expansion joints, the bell mouth, Inlet valve, PID/PLC Controlled Speed Governor, Control and Protection panels for Turbine and Generator, outgoing HT Panel, the mandatory spare parts, the best standard maintenance tools, inspection and training of Employer’s Engineers/technicians at the manufacturers works abroad and on job during installation, commissioning and test running of turbo generating sets.

| NAME OF SCHEME | Capacity (KW) | No. of Units | Gross head (m) | Net Head (m) | Discharge m3/sec | Main Penstock Pipe |  | Speed |  | Generation voltage (V) | Altitude (AMSL) | Turbine recommended |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Length (m) | Dia (m) | Rated speed (RPM) | Run Away (RPM) | Gen. voltage (V) |  |  |
| MHP DIZG | 230 | 01 | 33.5 | 33 | 0.845 | 55 | 0.66 | 750 | AS per design | 415 | 2515m | Francis |

Bidders must quote for the complete scope of work. Any bid covering partial scope of work will be rejected, considering as non-responsive, pursuant to Clause IB.24.

1.2	Source of Funds

The project is funded by European Commission (EU) under the Energy Plus. Civil works have already been under taken by AKRSP with the assistance of local community and construction work is in progress. It is intended that part of available funds under this programme will be applied to eligible payments under the Contract in PKR for which, this bidding document is issued.

IB.2	Eligible Bidders

2.1	Bidding is open to all firms and contractors meeting the following requirements:

a)	 The goods and auxiliary equipment/parts to be supplied in this contract shall be from eligible countries, where the turbo generators and auxiliary equipment are manufactured in compliance with International Standards with a specific established ''Quality Assurance Procedure'' according to ISO 9001.

IB.3	Eligible Goods and Services

3.1	All Goods and ancillary Services to be supplied under this Contract shall have their origin in eligible countries where turbo generators and auxiliary equipment are manufactured, having friendly relations with Pakistan and all expenditure made under the contract will be limited to such goods and services.

3.2	For purpose of this Clause, “origin” means the place where the Goods are mined, grown or produced or from where the ancillary services are supplied. Goods are produced when, through manufacturing, processing or substantial and major assembling of components, a commercially recognized product results that is substantially different in basic characteristics or in purpose or utility from its components.

3.3	The origin of Goods and Services is distinct from the nationality of the Bidder.

IB.4	Cost of Bidding

4.1	The bidder shall bear all costs associated with the preparation and submission of its bid and the Employer will in no case be responsible or liable for those costs, regardless of the conduct or outcome of the bidding process.

B.	BIDDING DOCUMENTS

IB.5	Contents of Bidding Documents

5.1	In addition to Invitations for Bids, the Bidding Documents are those stated below, and should be read in conjunction with any Addendum issued in accordance with Clause IB.7.

1.	Instructions to Bidders with Appendices

2.	Form of Bid & Schedules to Bid

Schedules to Bid are the following:

- Schedule A: Specific Works Data

- Schedule B: Work to be Performed by Subcontractors

- Schedule C: Proposed Programme of Works

- Schedule D: Deviations from Technical Provisions

- Schedule E: Deviations from Contractual Conditions

- Schedule F: Method of Performing Works

- Schedule G: Proposed Organization

- Schedule H: Integrity Pact

3.	Schedule of Prices

4.	Preamble to Conditions of Contract

5.	General Conditions of Contract

6.	Particular Conditions of Contract

7.	Standard Forms

Forms include the following:

(i)	Form of Bid Security

(ii)	Form of Contract Agreement

(iii)	Form of Performance Security

(iv)	Form of Bank Guarantee/Bond for Advance Payment

8.	Specifications - Special Provisions

9.	Specifications - Technical Provisions

10.	Drawings

5.2	The bidders are expected to examine carefully the contents of all the above documents. Failure to comply with the requirements of bid submission will be at the Bidder’s own risk. Pursuant to Clause IB.24, bids which are not substantially responsive to the requirements of the Bidding Documents will be rejected.

IB.6	Clarification of Bidding Documents

6.1	Requests for clarifications of the Bidding Documents can be submitted by e-mail. Requests will only be considered if received not later than fourteen (14) days prior to the deadline for the submission of Tenders.

Requests can be sent to:

Mr. Zeeshan Ali, Manager Engineering Branch

E-mail: zeeshan.ali@akdn.org, With copy to:

Mr. Mir Alam Manager Procurement

mir.alam@akdn.org

6.2	Employer will examine the request for clarification of the Bidding Documents which it receives not later than fourteen (14) days prior to the deadline for the submission of bids and if needed will issue the clarification/amendment of the Bidding Documents at least ten (10) days prior to the date of submission of Bids (without identifying the source of enquiry) to all prospective bidders who have obtained the Bidding Documents.

6.3	A pre-bid meeting will be held at client’s premises and/or through any online platform 14 days after Tender publishing. Date, time and link to the online platform of the meeting will be conveyed to the bidders through Email/ WhatsApp telephone.

IB.7	Amendment of Bidding Documents

7.1	At any time, about (7 days) prior to the deadline for submission of bids, the Employer may, for any reason, whether at his own initiative or in response to a clarification requested by a prospective bidder, modify the Bidding Documents by issuing addendum.

7.2	Any addendum thus issued shall be part of the Bidding Documents pursuant to Sub-Clause 7.1 hereof, and shall be communicated in writing to all purchasers of the Bidding Documents. Prospective bidders shall acknowledge receipt of each addendum in writing to the Employer. The bidder shall also confirm in the Form of Bid that the information contained in such addenda have been considered in preparing his bid.

7.3	To afford prospective bidders reasonable time in which to take an addendum into account in preparing their bids, the Employer may at its discretion extend the deadline for submission of bids in accordance with Clause IB.19.

C.	PREPARATION OF BIDS

IB.8	Language of Bid

8.1	The Bid prepared by the Bidder and all correspondence and documents relating to the Bid, exchanged by the Bidder and the Employer shall be written in the English language, provided that any printed literature furnished by the Bidder may be written in another language so long as accompanied by an English translation of its pertinent passages in which case, for purposes of interpretation of the Bid, the English translation shall govern.

IB.9	Documents Comprising the Bid

9.1	The bid prepared by the bidder shall comprise the following components:

(a)	Covering Letter

(b)	Form of Bid duly filled, signed and sealed, in accordance with Clause IB.17.

(c)	Schedules (A to H) to Bid duly filled and signed, in accordance with the instructions contained therein.

(d)	Schedule of Prices completed in accordance with Clauses IB.11 and 12.

(e)	Bid Security furnished in accordance with Clause IB.15.

(f)	Power of Attorney in accordance with Clause IB 17.5.

(g)	Joint Venture Agreement (if applicable).

(h)	Documentary evidence established in accordance with Clause IB.13 that the bidder is eligible to bid and is qualified to perform the contract if its bid is accepted.

(i)	Documentary evidence established in accordance with Clause IB.14 that the Goods and ancillary Services to be supplied by the bidder are eligible Goods and Services and conform to the Bidding Documents.

(j)	Bidders applying for eligibility for domestic preference in bid evaluation shall supply all information & evidence to establish the claim for domestic preference required to satisfy the criteria for eligibility as described in Clause IB.27. The particulars for domestic Goods prescribed in Appendix C to these Instructions shall also be filled in to substantiate claim for domestic preference.

(k)	Any other documents prescribed in Particular Conditions of Contract or Technical Provisions to be submitted with the bid.

IB.10	Form of Bid and Schedules

10.1	The bidder shall complete, sign and seal the Form of Bid, Schedules (A to H, or as modified) to Bid and Schedule of Prices furnished in the Bidding Documents and shall also enclose other information as detailed in Clause IB.9.

10.2	In preparing their bids, the bidders, whether local or foreign, shall enter in the Schedule of Prices ex-factory price for indigenously manufactured products and CIF price as well as customs duty and sales tax and other import charges for products to be imported from outside Pakistan.

IB.11	Bid Prices

11.1	The bidder shall fill up the Schedule of Prices attached to these documents indicating the unit rates and prices of the Works to be performed under the Contract. Prices on the Schedule of Prices shall be entered keeping in view the instructions contained in the Preamble to the Schedule of Prices.

11.2	The bidder shall fill in rates and prices for all items of the Works described in the Schedule of Prices. Items against which no rate or price is entered by a bidder will not be paid for by the Employer when executed and shall be deemed covered by rates and prices for other items in the Schedule of Prices.

11.3	The bidder’s separation of price components in accordance with Sub-Clause 11.1 above, will be solely for the purpose of facilitating the comparison of bids by the Employer and will not in any way limit its right to contract on any of the terms offered.

11.4	Unless otherwise stipulated in the Conditions of Contract, prices quoted by the bidder shall remain fixed during the bidder’s performance of the Contract and not subject to variation on any account. When the bidders are required to quote only fixed price(s) a bid submitted with an adjustable price quotation will be treated as non-responsive and rejected, pursuant to Clause IB.24.

11.5	Any discount offered shall be valid for at least the period of validity of the bid. A discount valid for lesser period shall be considered null and void.

IB.12	Currencies of Bid

12.1	Prices shall be quoted in the following currencies:

(a)	For Goods and Services which the bidder will supply, from abroad the prices shall be quoted in the PKR and will be paid in PKR.

IB.13	Documents Establishing Bidder’s Eligibility and Qualifications

13.1	Pursuant to Clause IB.9, the bidder shall furnish, as part of its bid, documents establishing the bidder’s eligibility to bid and its qualifications to perform the Contract if its bid is accepted.

13.2	The documentary evidence of the bidder’s eligibility to bid shall establish to the Employer’s satisfaction that the bidder, at the time of submission of its bid is from an eligible source country as defined under Clause IB.2.

13.3	The documentary evidence of the bidder’s qualification to perform the Contract if its bid is accepted, shall establish to the Employer’s/Engineer’s satisfaction:

- that, in the case of a bidder offering to supply Goods under the Contract which the bidder did not manufacture or otherwise produce, the bidder has been duly authorized by the Goods manufacturer or producer to supply the Goods to Pakistan;

- that the Bidder/Manufacturer has the financial, technical and production capability necessary to perform the Contract; and

- that, in the case of a bidder not doing business within Pakistan the bidder is or will be (if successful) represented by an agent in Pakistan equipped and able to carry out the Supplier’s maintenance, repair and spare parts stocking obligations prescribed by the Conditions of Contract and/or Technical Provisions.

13.4	(a)	Bidder/Manufacturer must possess and provide evidence of the following experience.

1.	General experience

2.	Particular experience

3.	Technical capability

The Bidder shall certify the capacity and capability of the plant (from which Goods are now offered) for manufacturing, quality assurance and testing facilities, qualified man-power and production/delivery of quality materials according to bid specifications and delivery requirements. Besides, such plant should have produced same items for at least Eight (8) years and such Goods 
 shall have proven successful in the field for at least Three (03) years and the bidder shall submit with the bid all necessary documentation in this regard. The Employer/Engineer will have the right to verify the particulars regarding the plant and other related information furnished with the bid and the joint venture as well as the partners thereof shall be liable for disqualification in the event of any mis-statement/mis-representation on their part.

The bidder shall furnish documentary evidence of qualification on the Form “Evidence of Bidder’s Capability” (Appendix B to these Instructions)

(b)	The bidder should have an average annual turnover in the last five years equal to or more than the Total Bid Price. Alternately, the bidder should have successfully completed in the last five years a Hydropower plants project having value equal to or higher than the total Bid Price.

13.5	Joint Venture

In order for a Joint Venture to qualify:

- At least one of the partners of joint venture shall satisfy the relevant experience criteria specified in Sub-Clause 13.4(a) hereinabove.

- All firms comprising the joint venture shall be legally constituted and shall meet the eligibility requirement of Sub-Clause 2.1 hereof.

- All partners of the joint venture shall at all times and under all circumstances be liable jointly and severally to Employer for the execution of the entire Contract in accordance with the Contract terms and conditions and a statement to this effect shall be included in the authorization mentioned under para (f) below as well as in the Form of Bid and Form of Contract Agreement (in case of a successful bidder).

- The Form of Bid, and in the case of successful bidder, the Form of Contract Agreement, shall be signed so as to be legally binding on all partners.

- One of the joint venture partners shall be nominated as being in-charge and this authorization shall be evidenced by submitting a power of attorney signed by legally authorized signatories of all the joint venture partners.

- The partner-in-charge shall be authorized to incur liabilities, receive payments and receive instructions for and on behalf of any or all partners of the joint venture.

- A copy of the agreement entered into by the joint venture partners shall be submitted with the bid stating the conditions under which it will function, its period of duration, the persons authorized to represent and obligate it and which persons will be directly responsible for due performance of the Contract and can give valid receipts on behalf of the joint venture, the proportionate participation of the several firms forming the joint venture, and any other information necessary to permit a full appraisal of its functioning. No amendments / modifications whatsoever in the joint venture agreement shall be agreed to between the joint venture partner without prior written consent of the Employer.

13.6	The Bidder shall propose, in order of his priority; plant, equipment or goods of not more than three Manufacturers. Employer at his own jurisdiction will evaluate the plant, equipment or goods of only one of such Manufacturers.

IB.14	Documents Establishing Goods’ Eligibility and Conformity to Bidding Documents

14.1	Pursuant to Clause IB.9, the bidder shall furnish, as part of its bid, documents establishing the eligibility and conformity to the Bidding Documents of all Goods and Services which the bidder proposes to perform under the Contract.

14.2	The documentary evidence of the Goods and Services eligibility shall establish to the Employer’s satisfaction that they will have their origin in an eligible source country as defined under Clause IB.3. A certificate of origin issued at the time of shipment will satisfy the requirements of the said Clause.

14.3	The documentary evidence of the Goods and Services’ conformity to the Bidding Documents may be in the form of literature, drawings and data and shall furnish:

- A detailed description of the Goods, essential technical and performance characteristics.

- Complete set of technical information, description data, literature and drawings as required in accordance with Schedule A to Bid, Specific Works Data. This will include but not be limited to the following:

(i)	A sufficient number of drawings, photographs, catalogues, illustrations and such other information as is necessary to illustrate clearly the significant characteristics such as general construction dimensions and other relevant information about the Goods to be furnished.

(ii)	Details of equipment and machinery with capacity.

(iii)	Any other information which is required for evaluation purposes.

(c)	A clause-by-clause commentary on Technical Provisions, provided with the Bidding Documents, demonstrating the Goods’ and Services’ substantial responsiveness to those Specifications or a statement of deviations and exceptions to the provisions of the Technical Provisions as required in Schedule D to Bid.

14.4	For purpose of the commentary to be furnished pursuant to Sub-Clause 14.3(c) above, the Bidder shall note that standards for workmanship, material and equipment, and references to brand names or catalogue numbers, designated by the Engineer in the Technical Provisions are intended to be descriptive only and not restrictive. The bidder may substitute alternative standards, brand names and/or catalogue numbers in its bid, provided that it demonstrates to the Engineer’s satisfaction that the substitutions are substantially equivalent or superior to those designated in the Technical Provisions. Copies of the standards proposed by the bidder other than those specified in the Bidding Documents shall be furnished.

IB.15	Bid Security

15.1	Each bidder shall furnish, as part of his bid, a Bid Security in the amount of minimum 2% of Bid price and should be in separate sealed envelope.

15.2	The Bid Security shall be, in the form of Deposit at Call from a scheduled bank in Pakistan or from a foreign bank duly counter guaranteed by a schedule bank in Pakistan in favor of the employer valid for a period 28 days beyond the bid validity date.

15.3	The Bid Security is required to protect the Employer against the risk of bidder’s conduct which would warrant the security’s forfeiture, pursuant to Sub-Clause 15.7 hereof.

15.4	Any bid not accompanied by an acceptable Bid Security shall be rejected by the Employer as non-responsive, pursuant to Clause IB.24.

15.5	The bid securities of unsuccessful bidders will be returned upon award of contract to the successful bidder or on the expiry of validity of Bid Security whichever is earlier.

15.6	The Bid Security of the successful bidder will be returned when the bidder has furnished the required Performance Security, pursuant to Clause IB.34 and signed the Contract Agreement, pursuant to Clause IB.35.

15.7	The Bid Security may be forfeited:

(a)	if a bidder withdraws his bid during the period of bid validity; or

(b)	if a bidder does not accept the correction of his Bid Price, pursuant to Sub-Clause 24.2 hereof; or

(c)	in the case of a successful bidder, if he fails to:

(i)	furnish the required Performance Security in accordance with Clause IB.34, or

(ii)	sign the Contract Agreement, in accordance with Clause IB.35.

IB.16	Validity of Bids

16.1	Bids shall remain valid for 180 days after the date of bid opening as prescribed in Clause IB.19.

16.2	In exceptional circumstances prior to expiry of original bid validity period, the Employer may request the bidders to extend the period of validity for a specified additional period which shall in no case be more than the original bid validity period. The request and the responses thereto shall be made in writing. A bidder may refuse the request without forfeiture of his Bid Security. A bidder agreeing to the request will be required to extend the validity of his Bid Security for the period of the extension, and in compliance with Clause IB.15 in all respects in which case, the Employer will be obligated to compensate the bidders, upon substantiation for their increase in costs (if it is a fixed price bid).

IB.17	Format and Signing of Bid

17.1	Bidders are particularly directed that the amount entered on the Form of Bid shall be for performing the Contract strictly in accordance with the Bidding Documents.

17.2	All Schedules to Bid are to be properly completed and signed.

17.3	No alteration is to be made in the Form of Bid nor in the Schedules thereto except in filling up the blanks as directed. If any alteration be made or if these instructions be not fully complied with, the bid may be rejected.

17.4	Each bidder shall prepare one (1) Original, of the documents comprising the bid as described in Clause IB.9 and clearly mark them “ORIGINAL” as appropriate. In the event of discrepancy between them, the original shall prevail.

17.5	The original and if copies of the bid shall be typed or written in indelible ink and shall be signed by a person or persons duly authorized to sign (in the case of copies, Photostats are also acceptable). This shall be indicated by submitting a written Power of Attorney authorizing the signatory of the bidder to act for and on behalf of the bidder. All pages of the bid shall be initialed and stamped by the person or persons signing the bid.

17.6	The bid shall contain no alterations, omissions or additions, except to comply with instructions issued by the Employer, or as are necessary to correct errors made by the bidder, in which case such corrections shall be initialed by the person or persons signing the bid.

17.7	Bidders shall indicate in the space provided in the Form of Bid their full and proper addresses at which notices may be legally served on them and to which all correspondence in connection with their bids and the Contract is to be sent.

17.8	Bidders should retain a copy of the Bidding Documents as their file copy.

D.	SUBMISSION OF BIDS

IB.18	Sealing and Marking of Bids

18.1	Each bidder shall submit his bid as under:

(a)	ORIGINAL or each COPY of the Bid shall be separately sealed and put in separate envelopes and marked as such.

(b)	The envelopes containing the ORIGINAL or COPIES will be put in one sealed envelope and addressed / identified as given in Sub- Clause 18.2 hereof.

18.2	The inner and outer envelopes shall;

(a)	Be addressed to the Employer at the address given in Sub-Clause 6.1 heretofore.

(b)	Bear the Project name, Loan No., Bid No. and Date of opening of Bid.

(c)	Provide a warning not to open before the time and date for bid opening.

18.3	The Bid shall be delivered in person or sent by registered mail at the address to Employer as given in Sub-Clause 6.1 heretofore.

18.4	In addition to the identification required in Sub-Clause 18.2 hereof, the inner envelope shall indicate the name and address of the bidder to enable the bid to be returned unopened in case it is declared “late” pursuant to Clause IB.20.

18.5	If the outer envelope is not sealed and marked as above, the Employer will assume no responsibility for the misplacement or premature opening of the bid.

18.6     The procedures for submission of proposals through email shall be:

The Bidder must archive and encrypt the folder. Bidders shall use PASSWORDS for the bid. The password should be kept securely for the entire procurement process and only be disclosed to the Employer as per instructions below. Disclosure of passwords by the Bidders is compromising the confidentiality principle and may result in the rejection of its proposal.

We recommend using the free 7-Zip (https://www.7-zip.org) (Archive format: zip) with AES-256 (Encryption method: AES-256). For security reasons, the password shall have at least 12 characters.

Prior to the Bids’ Submission Deadline, Bidder sends the Bid as attachment to the e-mail to “procurement_akrsppk@akdn.org”

. The e-mail message, including all attachments, must not exceed 20MB. The subject line of the e-mail message should specify the Tender Name. Passwords must NOT be sent at this stage. Bids containing passwords are compromising the confidentiality principle and are subject to rejection. Bidders must safely store the zip archives as submitted for the entire procurement process.

Important Note: If for technical reasons the archived Bids exceeds the recommended size (20MB), then the archives must be split in volumes when archiving with each volume hashed separately and submitted in individual e-mails. In this case e-mails shall be numbered and all volumes be received by the Employer not later than the Bids’ submission deadline.

The Employer shall confirm the receipt of each Bid by e-mail with verification of integrity of the Bids in the following 8 working hours. Therefore, the Bidders are recommended to send their proposals in advance to allow the Bidder to confirm the receipt before the submission deadline. If such confirmation is not received by the Bidder in the specified timeframe, the Bidder shall contact the Employer for clarifications.

The Bidders shall be available to interact with the Employer via e-mail, phone and online conferencing tool proposed by the Employer for at least 2 hours starting with the Bids submission deadline.

Both Employer and Bidders should check Inbox and SPAM folders for the receipt of electronic Bids and any related communication.

In case the Bidder submits electronic Bid, the hard copies of specific documents (Bid security, Processing fee and other related documents) shall also be sent as per the procedures of current document no later than fourteen (14) days after Bid opening date.

IB.19	Deadline for Submission of Bids

19.1	(a)	Bids must be received by the Employer at the address specified in Sub-Clause 6.1 hereof not later than the time and date stipulated in the Invitation for Bids.

(b)	Bids with charges payable will not be accepted, nor will arrangements be undertaken to collect the bids from any delivery point other than that specified above. Bidders shall bear all expenses incurred in the preparation and delivery of bids.

(c)	Where delivery of a bid is by mail and the bidder wishes to receive an acknowledgment of receipt of such bid, he shall make a request for such acknowledgment in a separate letter attached to but not included in the sealed bid package.

(d)	Upon request, acknowledgment of receipt of bids will be provided to those making delivery in person or by messenger.

19.2	Bids submitted through telegraph, telex, fax shall not be considered.

19.3	The Employer may, at his discretion, extend the deadline for submission of bids by issuing an addendum in accordance with Clause IB.7, in which case all rights and obligations of the Employer and the bidders previously subject to the original deadline will thereafter be subject to the deadline as extended.

IB.20	Late Bids

20.1	(a)	Any bid received by the Employer after the deadline for submission of bids prescribed in Clause IB.19 will be returned unopened to such bidder.

(b)	Delays in the mail, delays of person in transit, or delivery of a bid to the wrong office shall not be accepted as an excuse for failure to deliver a bid at the proper place and time. It shall be the bidder’s responsibility to determine the manner in which timely delivery of his bid will be accomplished either in person, by messenger or by mail.

IB.21	Modification, Substitution and Withdrawal of Bids

21.1	Any bidder may modify, substitute or withdraw his bid after bid submission provided that modification, substitution or written notice of the withdrawal is received by the Employer prior to the deadline for submission of bids.

21.2	The modification, substitution or notice for withdrawal of any bid shall be prepared, sealed, marked and delivered in accordance with the provisions of Clause IB.18 with the outer and inner envelopes additionally marked “MODIFICATION”, “SUBSTITUTION” or “WITHDRAWAL”, as appropriate.

21.3	Withdrawal of a bid during the interval between the deadline for submission of bids and the expiration of the period of bid validity specified in the Form of Bid may result in forfeiture of the Bid Security pursuant to Clause IB.15.

E.	BID OPENING AND EVALUATION

IB.22	Bid Opening

22.1	A committee consisting of nominated members by the Employer and by the Engineer will open the bids, including withdrawals, substitution and modifications made pursuant to Clause IB.21, in the presence of bidders’ representatives who choose to attend, at the time, date and location stipulated in the Invitation for Bids.

The bidders’ representatives who are present shall sign in a register evidencing their attendance.

22.2	Envelopes marked “MODIFICATION”, “SUBSTITUTION” or “WITHDRAWAL” shall be opened and read out first and the name of the Bidder shall be read out. Bids for which an acceptable notice of withdrawal has been submitted pursuant to Clause IB.21 shall not be opened.

22.3	The bidder’s name, Bid Prices, unit rates, any discount and price of any Alternate Proposal(s), bid modifications, substitutions and withdrawals, the presence or absence of Bid Security, and such other details as the Employer at its discretion may consider appropriate, will be announced by the Employer at the bid opening. The Employer will record minutes of bid opening.

Any Bid Price or discount which is not read out and recorded at bid opening will not be taken into account in the evaluation of bid.

22.4	Discounts offered for lesser period than the bid validity shall not be considered in evaluation.

IB.23	Clarification of Bids

23.1	To assist in the examination, evaluation and comparison of Bids the Employer/Engineer may, at its discretion, ask the Bidder for a clarification of its Bid. The request for clarification and the response shall be in writing and no change in the price or substance of the Bid shall be sought, offered or permitted.

IB.24	Preliminary Examination & Determination of Responsiveness of Bids

- Prior to the detailed evaluation of bids, pursuant to Clause IB.26,

- the Employer will examine the Bids to determine whether;

(i) 	The Bid is complete and does not deviate from the scope,

(ii)	Any computational errors have been made,

(iii)	Required securities have been furnished,

(iv) 	The documents have been properly signed,

(v) 	The Bid is valid till required period,

(vi) 	The Bid prices are firm during currency of contract if it is a fixed price bid,

(Vii) 	Completion period offered is within specified limits,

(viii) 	The Bidder/Manufacturer is eligible to Bid and possesses the requisite experience,

(ix) 	The Bid does not deviate from basic technical requirements and

(x) 	The Bids are generally in order.

(b)	A bid is likely not to be considered, if;

- it is unsigned,

- its validity is less than specified,

- it is submitted for incomplete scope of work,

- it indicates completion period later than specified,

- it indicates that Works and materials to be supplied do not meet eligibility requirements,

- it indicates that Bid prices do not include the amount of income tax,

(c)	A bid will not be considered, if;

(i)	it is not accompanied with bid security,

(ii)	it is submitted by a bidder who has participated in more than one bid,

(iii)	it is received after the deadline for submission of bids,

(iv)	it is submitted through fax, telex, or telegram,

(v)	it indicates that prices quoted are not firm during currency of the contract whereas the bidders are required to quote fixed price(s),

(vi)	the bidder refuses to accept arithmetic correction,

(vii)	it is materially and substantially different from the Conditions/Specifications of the Bidding Documents.

24.2	Arithmetical errors will be rectified on the following basis:

If there is a discrepancy between the unit price and total price that is obtained by multiplying the unit price and quantity, the unit price shall prevail and the total price shall be corrected. If there is a discrepancy between the words and figures the amount in words shall prevail. If there is a discrepancy between the total Bid price entered in Form of Bid and the total shown in Schedule of Prices Summary, the amount stated in the Form of Bid will be corrected by the Employer/Engineer in accordance with the Corrected Schedule of Prices.

If the Bidder does not accept the corrected amount of Bid, his Bid will be rejected and his Bid Security forfeited.

24.3	Prior to the detailed evaluation, pursuant to Clause IB.26 the Employer/Engineer will determine the substantial responsiveness of each Bid to the Bidding Documents. For purpose of these Clauses, a substantially responsive Bid is one which conforms to all the terms and conditions of the Bidding Documents without material deviations.

A material deviation or reservation is one

(i)	which affects in any substantial way the scope, quality or performance of the Works.

(ii)	which limits in any substantial way, inconsistent with the Bidding Documents, the Employer’s rights or the bidder’s obligations under the Contract; or

(iii)	whose rectification/adoption would affect unfairly the competitive position of other bidders presenting substantially responsive bids.

The Employer’s/Engineer’s determination of a Bid’s responsiveness will be based on the contents of the Bid itself without recourse to extrinsic evidence.

24.4	A Bid determined as substantially non-responsive will be rejected and will not subsequently be made responsive by the Bidder by correction of the non-conformity.

24.5	Any minor informality or non-conformity or irregularity in a Bid which does not constitute a material deviation may be waived by Employer, provided such waiver does not prejudice or affect the relative ranking of any Bidder.

IB.25	Conversion to Single Currency

25.1	To facilitate evaluation and comparison, the Employer/Engineer will convert, all Bid Prices expressed in the amount in various currencies into PKR based on the exchange rates published/authorized by State Bank of Pakistan and applicable to similar transactions, on the date of the opening of the Bids.

IB.26	Detailed Evaluation of Bids

26.1	The Employer/Engineer will evaluate and compare only the bids previously determined to be substantially responsive pursuant to Clause IB.24 as per requirements given hereunder.

26.2	Evaluation and Comparison of Bids

(a)	Bids will be evaluated for each item and/or complete scope of work.

(b)	Basis of Price Comparison

The prices will be compared on the basis of the Evaluated Bid Price pursuant to Para (e) herein below.

(c)	Technical Evaluation

It will be examined in detail whether the Goods offered by the bidder comply with the Technical Provisions of the Bidding Documents. For this purpose, the bidder’s data submitted with the bid will be compared with the specific work data prescribed by the Employer and technical features/criteria of the Goods detailed in the Technical Provisions. Other technical information submitted with the bid regarding the Scope of Work will also be reviewed.

(d)	Commercial Evaluation

It will be examined in detail whether the bids comply with the commercial/contractual conditions of the Bidding Documents. It is expected that no major deviation/stipulation shall be taken by the bidders.

(e)	Evaluated Bid Price

In evaluating the bids, the Employer will determine for each bid in addition to the Bid Price, the following factors (adjustments) in the manner and to the extent indicated below to determine the Evaluated Bid Price:

(i)	making any correction for errors pursuant to Sub-Clause 24.2 hereof.

(ii)	excluding Provisional Sums, if any, but including priced Day work.

(iii)	making an appropriate adjustment for any other acceptable variation or deviation.

26.3	Evaluation Methods

Pursuant to Sub-Clause 26.2, Para (e)(iii) following evaluation methods for price adjustments will be followed:

Price Adjustment for Completeness in Scope of Work

In case of omission in the scope of work of a quoted item no price adjustment for the omitted item(s) shall be applied provided that the Bidder has mentioned in his bid that the same is covered in any other item.

The price adjustment shall not justify any additional payment by the Employer. The price(s) of omitted item(s) shall be deemed covered by other prices of the Schedule of Prices.

26.4	If the bid of the successful bidder is seriously unbalanced in relation to the Employer’s estimate of the cost of work to be performed under the Contract, the Employer may require the bidder to produce detailed price analyses for any or all items of the Schedule of Prices to demonstrate the internal consistency of those prices with the construction methods and schedule proposed. After evaluation of the price analyses, the Employer may require that the amount of the Performance Security set forth in Clause IB.34 be increased at the expense of the successful bidder to a level sufficient to protect the Employer against financial loss in the event of default of the successful bidder under the Contract.

IB.27	Process to be Confidential

27. 1	Subject to Clause 23 heretofore, no Bidder shall contact Employer and/or Engineer on any matter relating to its Bid from the time of the Bid opening to the time the bid evaluation result is announced by the Employer. The evaluation result shall be announced at least ten (10) days prior to award of Contract. The announcement to all bidders will include table(s) comprising read out prices, discounted prices, price adjustments made, final evaluated prices and recommendations against all the bids evaluated.

27.2	Any effort by a Bidder to influence Employer and/or Engineer in the Bid evaluation, Bid comparison or Contract Award decisions may result in the rejection of his Bid. Whereas any bidder feeling aggrieved may lodge a written complaint not later than fifteen (15) days after the announcement of the bid evaluation result; however, mere fact of lodging a complaint shall not warrant suspension of the procurement process.

F.	AWARD OF CONTRACT

IB.28.	Post-Qualification

28.1	The Employer, at any stage of the bid evaluation, having credible reasons for or prima facie evidence of any defect in supplier’s or contractor’s capacities, may require the suppliers or contractors to provide information concerning their professional, technical, financial, legal or managerial competence whether already pre-qualified or not:

Provided that such qualification shall only be laid down after recording reasons therefor in writing. They shall form part of the records of that bid evaluation report.

28.2	The determination will take into account the bidder’s financial, technical and production capabilities. It will be based upon an examination of the documentary evidence of the bidder’s qualification submitted under Appendix B to Instructions to Bidders "Evidence of Bidder’s Capability" by the bidder pursuant to Clause IB.13, as well as such other information as required under the Bidding Documents.

28.3	An affirmative determination will be a pre-requisite for award of the Contract to the most advantageous evaluated Bid Price. A negative determination will result in rejection of that bidder’s bid in which event, Employer will proceed to undertake a similar determination of the next most advantageous bidder's capabilities to perform the Contract satisfactorily.

IB.29	Award Criteria

29.1	Subject to Clause IB.32, the Employer will award the Contract to the bidder whose bid has been determined to be substantially responsive to the Bidding Documents and who has offered the most advantageous evaluated Bid Price, provided that such bidder has been determined to be qualified to satisfactorily perform the Contract in accordance with the provisions of Clause IB.29.

IB.30	Employer’s Right to Vary Quantities

30.1	Employer reserves the right at the time of award of Contract to increase or decrease by up to 15% the quantity of goods and services specified in the Schedule of Prices without any change in the unit price or other terms and conditions.

IB.31	Employer’s Right to Accept any Bid and to Reject any or all Bids

31.1	Notwithstanding Clause IB.30, the Employer reserves the right to accept or reject any bid, and to annul the bidding process and reject all bids, at any time prior to award of Contract, without thereby incurring any liability to the affected bidders or any obligation to inform the affected bidders of the grounds for the Employer’s action except that the grounds for its rejection shall upon request be communicated, to any bidder who submitted a bid, without justification of grounds.  Rejection of all bids shall be notified to all bidders promptly.

31.2	No negotiations with the bidder having been evaluated as the most advantageous evaluated Bid responsive or any other bidder shall be permitted. However, the Employer may have clarification meeting(s) to get clarify any item(s) in the bid evaluation report.

IB.32	Notification of Award

32.1	Prior to expiration of the period of bid validity prescribed by the Employer, the Employer will notify the successful bidder in writing (“Letter of Acceptance”) that his bid has been accepted. This letter shall name the sum which the Employer will pay the Contractor in consideration of the execution and completion of the Works by the Contractor as prescribed by the Contract (hereinafter and in the Conditions of Contract called the “Contract Price”).

32.2	The Letter of Acceptance and its acceptance by the bidder will constitute the formation of the Contract, binding the Employer and the Bidder till signing of the formal Contract Agreement.

32.3	Upon furnishing by the successful bidder of a Performance Security, the Employer will promptly notify the other bidders that their bids have been unsuccessful and return their bid securities.

IB.33	Performance and Advance Security

33.1	The successful bidder shall furnish to the Employer Performance and Advance Security in the form and the amount stipulated in the Conditions of Contract within a period of twenty-eight (28) days after the receipt of Letter of Acceptance.

33.2	Failure of the successful bidder to comply with the requirements of Sub-Clause IB.34.1 or Clause IB.35 or Clause IB.43 shall constitute sufficient grounds for the annulment of the award and forfeiture of the Bid Security.

IB.34	Signing of Contract Agreement

34.1	Within fourteen (14) days from the date of furnishing of acceptable Performance Security under the Conditions of Contract, the Employer will send to the successful bidder the Form of Contract Agreement provided in the Bidding Documents, duly filled in and incorporating all agreements between the parties for signing and return it to the Employer.

34.2	The formal Agreement between the Employer and the successful bidder shall be executed within fourteen (14) days of the receipt of such Form of Contract Agreement by the successful bidder from the Employer.

G. ADDITIONAL INSTRUCTIONS

IB.35	Instructions not Part of Contract

35.1	Bids shall be prepared and submitted in accordance with these Instructions which are provided to assist bidders in preparing their bids, and do not constitute part of the Bid or the Contract Documents.

IB.36	Contract Documents

36.1	The Documents which will be included in the Contract are listed in the Form of Contract Agreement set out in these Bidding Documents.

IB.37	Sufficiency of Bid

37.1	Each bidder shall satisfy himself before Bidding as to the correctness and sufficiency of his Bid and of the rates and prices entered in the Schedule of Prices. Except insofar as it is otherwise expressly provided in the Contract, the rates and prices entered in the Schedule of Prices shall cover all his obligations under the Contract and all matters and things necessary for the proper completion of the Works.

IB.38	One Bid per Bidder

38.1	Each bidder shall submit only one bid either by himself, or as a partner in a joint venture. A bidder who submits or participates in more than one bid (other than alternatives pursuant to Clause IB.41) will be disqualified and bids submitted by him shall not be considered for evaluation and award.

IB.39	Bidder to Inform Himself

39.1	The bidder is advised to obtain for himself at his own cost and responsibility all information that may be necessary for preparing the bid and entering into a Contract for execution of the Works. This shall include but not limited to the following:

(a)	inquiries on Pakistani Income Tax/Sales Tax to the Commissioner of the Income Tax and Sales Tax, CBR Pakistan.

(b)	inquiries on customs duties and other import taxes, to the concerned authorities of Customs and Excise Department.

(c)	information regarding port clearance facilities, loading and unloading facilities, storage facilities, transportation facilities and congestion at Pakistan seaports.

(d)	investigations regarding transport conditions and the probable conditions which will exist at the time the Goods will be actually transported.

IB.40	Alternate Proposals by Bidder

40.1	Should any bidder consider that he can offer any advantage to the Employer by a modification to the designs, specifications or other conditions, he may, in addition to his bid to be submitted in strict compliance with the Bidding Documents, submit any Alternate Proposal(s) containing (a) relevant design calculations; (b) technical specifications; (c) proposed construction methodology; and (d) any other relevant details / conditions, provided always that the total sum entered on the Form of Bid shall be that which represents complete compliance with the Bidding Documents.

40.2	Alternate Proposal(s), if any, of the most advantageous evaluated Bid Price evaluated responsive bidder only may be considered by the Employer as the basis for the award of Contract to such bidder.

IB.41 	Local Conditions

41.1	Bidder must verify and supplement by his own investigations the information about site and local conditions. However, Employer will assist the Bidder wherever practicable and possible.

IB.42	Integrity Pact

The Bidder shall sign and stamp the Integrity Pact provided at Schedule-H to Bid in the Bidding Document for all Federal Government procurement contracts exceeding Rupees ten million. Failure to provide such Integrity Pact shall make the bid non-responsive.

Appendix A to

Instructions to Bidders

NAME OF ELIGIBLE COUNTRIES

[User to list down the Name of eligible countries as per Clause 2 of Instructions to Bidders]

All Goods and ancillary Services to be supplied under this Contract shall have their origin in eligible countries where turbo generators and auxiliary equipment are manufactured, having friendly relations with Pakistan except Israel and all expenditure made under the contract will be limited to such goods and services.

Appendix B to

Instructions to Bidders

EVIDENCE OF BIDDER’S CAPABILITY

[Note: Bidders to provide the following information with the bid separately and indicate herein its references where this information is available.]

Sr.No.		Information to be Supplied				Bid References

1. 	Name of bidder, business address and country of incorporation.

2. 	Type of firm whether individually owned, partnership, corporation or joint venture and the names of its owners or partners.

3. 	The annual reports or qualification statements giving general description of the firm, sort of business carried out, balance sheets, profit and loss statements, turn over and business done by the firm, duly authenticated, for the last three (3) years.

4.	Location and address of manufacturing facilities.

5. 	Full description of factories owned and the annual manufacturing capacities of various items made therein.

6. 	Details of the factory or factories where the offered equipment is proposed to be manufactured. This description should include the facilities and capacities of the particular factories including testing facilities and the processes used in manufacturing and testing. Where parts or components are purchased from outside, the details of equipment purchased and the names and experience record of the suppliers.

7. 	Detailed description of the quality control testing and research facilities. If the equipment is manufactured under license, the name of the licenser and details of the licensing arrangements, such as the duration of the license, the facilities provided to the bidder by the licenser and whether future improvements are available or not etc. A copy of the license agreement may be attached.

8. 	Names, qualifications and experience of the key technical personnel.

9. 	The time since the manufacturer has been in this business and the time since he has been doing work of similar nature.

10. 	The time since the particular equipment offered has been manufactured and the time for which it has been in service. The manufacturer shall have the following experience.

i)	General Experience

ii)	Technical Capacity

iii)	08 years’ experience in production

iv)	03 years successful operation

11. 	Reference lists of similar works done by the bidder in its country and abroad indicating the name of customer, description and quantity of product, year of supply and the approximate value.

12. 	Details of projects under execution and future contractual commitments (for each partner, in case of a joint venture).

- Banking reference, names of banks and addresses may be given to whom reference regarding financial capability of the bidder may be made, with authority to make inquiries from the bidder’s bankers and clients regarding any financial and technical aspects (for each partner, in case of a joint venture).

14. 	Information on any litigation or arbitration resulting from contracts completed or under execution by the bidder over the last ten (10) years. The information shall indicate the parties concerned, the matter of dispute, the disputed amounts and the result thereof (for each partner, in case of a joint venture).

Appendix C to

Instructions to Bidders

Domestic Goods (Value added in Pakistan)

[Bidders claiming eligibility for domestic preference should fill in for supply items only, all columns hereunder and provide necessary documentation to substantiate their claim]

| Sr. No. | DELETED Description of Indigenous Goods | Unit | Qty | Total Price of Goods Ex-Factory | Domestic value added in the manufacturing cost as percentage of Ex-Factory Price | Amount of value addition |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| Total in columns 5 & 7 |  |  |  |  |  |  |

Computations:

A. Total amount of Value Addition (from Col.7) 		               _______________

B.	Total Ex-Factory Price of Indigenous Goods (from Col.5)	_______________

- Total DDP Price of imported supply items			___________

- Total Price of supply items [B+C]				___________

- % of value addition = [(A/D)x100] 				_______%

- Domestic Preference =(15,20 or 25)% of B			_______________

FORM OF BID AND SCHEDULES TO BID

FORM OF BID

(LETTER OF OFFER)

Bid Reference No. ________________

________________________________________

________________________________________

(Name of Works)

To:

_______________________________

_______________________________

_______________________________

Gentlemen,

1.	Having examined the Bidding Documents including Instructions to Bidders, Conditions of Contract, Specifications, Drawings, Schedule of Prices and Addenda Nos. _________________________ for the execution of the above-named Works, we, the undersigned, being a company doing business under the name of and address ______________________________________________ __________________________________________________________________
and being duly incorporated under the laws of ____________________________ hereby offer to execute and complete such Works and remedy any defects therein in conformity with the said Documents including Addenda thereto for the Total Bid Price comprising PKR Component of ______________ (________________________________________________________________)or such other sum as may be ascertained in accordance with the said Documents.

2.	We understand that all the Schedules attached hereto form part of this Bid.

3.	As security for due performance of the undertakings and obligations of this Bid, we submit herewith a Bid Security in the amount of ____________ ________________________ drawn in your favour or made payable to you and valid for a period twenty-eight (28) days beyond the period of validity of Bid.

4.	We undertake, if our Bid is accepted, to commence the Works and to deliver and complete the whole of the Works comprised in the Contract within the time(s) stated in Preamble to the Conditions of Contract.

5.	We agree to abide by this Bid for the period of ______ days from the date fixed for receiving the same and it shall remain binding upon us and may be accepted at any time before the expiration of that period.

6.	Unless and until a formal Agreement is prepared and executed, this Bid, together with your written acceptance thereof, shall constitute a binding contract between us.

7.	We undertake, if our Bid is accepted, to execute the Performance Security referred to in Clause 10 of Conditions of Contract for the due performance of the Contract.

8.	We understand that you are not bound to accept the lowest or any Bid you may receive.

9.	We do hereby declare that the Bid is made without any collusion, comparison of figures or arrangement with any other person or persons making a Bid for the Works.

10.	We confirm, if our Bid is accepted, that all partners of the joint venture shall be liable jointly and severally for the execution of the Contract and the composition or the constitution of the joint venture shall not be altered without the prior consent of the Employer. (Please delete in case of Bid from a single firm).

Dated this _______________________day of ____________________20______

Signature ________________in the capacity of _______________________duly

authorized to sign bids for and on behalf of ____________________________

(Name of Bidder in Block Capitals)

(Seal)

Address _____________________________________________________________________

_____________________________________________________________________

_____________________________________________________________________

Witness:

(Signature)___________________________________________________________

(Name)______________________________________________________________

Address:_____________________________________________________________

_____________________________________________________________________

Occupation____________________________________________________________

SCHEDULES TO BID INCLUDE THE FOLLOWING:

- Schedule A to Bid: Specific Works Data

- Schedule B to Bid: Work to be Performed by Subcontractors

- Schedule C to Bid: Proposed Programme of Works

- Schedule D to Bid: Deviations from Technical Provisions

- Schedule E to Bid: Deviations from Contractual Conditions

- Schedule F to Bid: Method of Performing Works

- Schedule G to Bid: Proposed Organization

- Schedule H to Bid: Integrity Pact

# SCHEDULE-A TO BID

# SPECIFIC WORKS DATA

(Proforma for specific Data to be prepared and incorporated by the Employer which will be filled in by the bidders)

ITEM WISE Technical Specifications

| Sl no. | Items | Required Specifications |
| --- | --- | --- |
| 1 | Designing, manufacturing, supply, installation, commissioning and testing of Horizontal Shaft Francis turbine 335 hp (imported) with flywheel system complete in all respect. With the following parameters: - - Gross head: 33.5 m - Net head: 33 m - Rated discharge: 0.845 m3/sec - Rated speed: 750 rpm - Runaway Speed: 1500-1600 rpm Note: For the Calculation of GD2 value, the Penstock length may be considered as 55 meters and the dia is 0.66 meters | - Turbine’s efficiency shall be not less than 92% - Material composition of runner and wicket gates shall be: 13:4 (Cr Ni) - Material and metallurgical test reports must be prepared complete in all respect, in English language and produced to the Employer inspection team, during factory acceptance test at manufacturer premises. - In order to optimize the turbine efficiency, the spiral casing should be designed by reducing the cross-sectional area gradually from inlet to the end of the spiral so that the water may be entered to the runner vanes with equal pressure to avoid resonance - The design calculations for specific speed and the rated speed of the turbine must be shared with the Client before finalization of the design. The draft tube should also be properly designed so that the pressure head of the water may be converted to velocity-head flowing from narrow area of the draft tube to the larger area adding kinetic energy of the runner. The length of the draft tube and the suction head (Hs) should be kept after detailed deliberation to ensure smooth flow, minimize turbulence and to prevent cavitation eventually. |
| 2 | Designing, manufacturing, supply, installation, commissioning and testing of PID/PLC-based Auto Control Speed Governor, including (manual control option) digital Control Panel with control wirings complete in all respect | - Electro-Hydraulic type speed governor with auto and manual facility including provision of hand wheel to open and close the servomotor manually if any time required. - PID/PLC speed controller with all protection provisions. The control system must include but not limited to the modern HMI interface, accumulator, pump, bidirectional valves and hydraulic system - Dashpot with droop setting value from 0 to 10% for the adjustment of governor’s sensitivity - The response time and settling time for the speed control should be set so, as the transients developed in the unit speed during abnormal operation must die off in 1 to 2 seconds. - The frequency transient spectrum must not be more than ± 2 Hz (48cps-to52cps) |
| 3 | Designing, manufacturing, supply, installation, commissioning and testing of Three Phase Brushless Synchronous Alternator, with self-excitation system complete in all respect, including voltage governor, to be installed at an elevation of over 2000 meters, with the following parameters: - - Power ratings: 285 kVA - Power factor: 0.80 - Speed: 750 rpm - Frequency: 50 cps - Number of poles: 8 Nos - Generation voltage: 415 volts - Neutral point permanently grounded | - Insulation Class: - - For Stator Winding the insulation class shall be Class-F (155 0C) and the insulation system shall consist of mica-based taps, with high grade varnish and vacuum pressure impregnation (VPI) - For Stator Winding the insulation class shall be Class-F (155 0C) and the insulation system shall consist of mica- taps, with epoxy varnish impregnation and mechanical protection as required. - Manufacturer shall guarantee winding hot-spot temperature do not exceed Class F limits under rated continuous load bat specified ambient temperature. - Cooling system: - Temperature Sensing: - - Through PT 100, installed in the windings and the output shown in the control panel through digital meters in 0c - Cooling Method: Natural Air Cooling. |
| 4 | Designing, manufacturing, supply, installation, commissioning and testing of Butterfly type Inlet Valve, complete in all respect including expansion joints, connection pipes and flanges for laidback interfacing with Spiral Casing of Francis Turbine | - Electric motor operated with remote control and manual operation option as well. - Nominal inlet dia (DN) of the valve must be interfaceable with the penstock flange dia equal about 0.660 meter - Nominal Pressure (PN) is 8 bar or 0.8mpa (it is minimum possible) |
| 5 | Manufacturing supply installation / fixing commissioning & testing of 11 KV Protection panel incorporated with 630 amp. VCB, multifunction digital protection relay, including overcurrent, short circuit and earth fault trip protections. PT operated volt meter, CT operated ampere meter along with sector switches, CTs and PTs, including the outgoing Energy Meter. | - Motorized VCB (ABB-Italy) 630 Amps, rated voltage 12 KV, withdrawable type, operating voltage 11KV, 25KA. Bil 36/95 KV, shunt coil open and close (110vdc), motor mechanism (220 vac), digital Over Current, Earth fault & Short Circuit Protection Relay (ABB Model rex-610), energy meter (Bluestar) including all other accessories enclosed in metal clade steel panel, complete in all respect |
| 6 | Designing, manufacturing, supply, installation, commissioning and testing of Generator Control Panel, including but not limited to Excitation Voltage Regulator/Control (AVR) module, and temperature control module. Complete in all respect | - Metal Clad control panel, enclosing low voltage air circuit breaker: 500 Amps capacity including overload, short circuit, over voltage and under voltage protections, minimum with automatic and manual trigger mechanism. - Incorporated with digital and analog volt meters, ampere meters, power factor meter, kilowatt meter, thermistor relay, frequency meter. - Along with digital indication/annunciation provisions complete in all respects. |
| 7 | Procurement and Supply of Special Tools for the maintenance of Electrical & Mechanical Equipment including but not limited to: - Testing instruments for electrical equipment - Tool kits for Electrical and mechanical equipment, spare parts and other allied accessories - Spare Parts | - Clamp on meter for AC/DC Current measuring, with measuring current up to 1000 amps DC/AC. |
|  |  | - Sets of special Screw drivers and voltage testers, Double end Fork spanners of different sizes, - Double ends flat spanners of different sizes - Double ends ring spanners of different sizes - Screw and pipe wrenches of different sizes - Runner dismantling tools set and socket wrench box for all the big sizes of nuts installed on the generator turbine and other accessories Note: all the above tools must me compatible for nut bolts and screws used in the current plat. |
|  |  | - See Section: Spares Parts and Tools for the Unit |
| 8 | Commercial operation and maintenance of the same power plant for six months after completion | - To provide skilled and well-trained staff to run the power plant, on commercial basis, round the clock, for the supply of uninterrupted electricity to the connected consumer for 6 months. - This staff will also be responsible for the training of local operators and supporting staff in the operation of power plant and necessary equipment, throughout the defect liability period validity, as per contract agreement. - This staff will leave the plant if AKRSP deems satisfied with the capacity of local operators to carryout regular maintenance of the power plant. |

- Spares Parts and Tools for the Unit

i)	Spare parts for Francis turbine

01. Runner 							01 No

02. Guide Vanes 							01 Set

03. Seal rings for inlet valve 					03 Sets

04. Guide vane seals, O-ring 					02 Sets

05. Seals O-ring, belts, for power pack				02 sets

06.	serve motor.							01 No

07. water control valves						06 Nos

08. Guide vane locking mechanism 				02 Sets

09. Water pressure gauges					02 Nos

10. Oil pressure gauges						02 Nos

11. Solenoid valve (Governor)					01 No

12 Governor oil pump						01 No

13.Nitrogen Bags for Governors					02 Nos

ii)	Spare parts for Generator

- Bearing 							02 Sets

- AVR cards							02 No

- Diodes 							02 Sets

- Rotating rectifiers						02 Sets

- PTs/ CTs							01 Set

- Varistor 							02 Sets

- Miniature switches						03 Nos

iii)	Spare parts for Protection Relays

- Over Current Relays 						01 No

- Short circuit Relay 						01 No

- Over / under frequency Relay				01 No

- Reverse power Relay						01 No

- Battery charger						01 Set

- Differential protection (03 phases) Relay			01 No

- De- excitation Relay						01 No

- Earth fault Relay						01 No

- Thermistor Relay 						01 No

- Erection, testing and maintenance tools

- Hydraulic jack, plats for mounting and dismantling of flywheel	01 Set

- Hydraulic puller for mounting/ dismounting or runner. 		01 Set

- Spanners of size 10 mm to 40 mm 				02 Sets

- Socket sets 							01 No

- Torque wrench							02 Sets

- Plier set								02 Sets

- Allen key set							01 Set

- Filler gauge 							01 No

- Adjustable wrench 6inch 					02 Nos

- Adjustable wrench 10inch					01 Set

- Dial indicator							03 Nos

- Iron Hammers (1 kg, 3 kg, 5 kg)					02 Nos

- Plastic Hammers (small and large) 				02 Nos

- Chisel 								01 No

- Electric drill machine with drill bit set 				01 Set

- Electric grinder 							01 No

- Spirit level 							01 No

- Tri square (Large size)						01 No

- File set 								01 Set

- Grease gun 							01 No

- Scrape (flat & angular)						02 Nos

- Pipe wrenches (small, medium & large)				03 Nos

- Small socket set for diode 					01 Set

- Knife and scissor set 						01 Set

- Special tools for governor 					01 Set

SITE DATA AND SPECIFIC Technical Specifications

| 01. | Name of Project | : | Rehabilitation and Upgradation of Dizg 230KW MHP at Yukum, Yarkhoon Valley District Upper Chitral. |
| --- | --- | --- | --- |
| 02. | Location | : | 155 KM from Chitral |
| 03. | Road classification | : | Truck able till Brep village followed by Jeepable road 22km |
| 04. | Altitude | : | 2515m AMSl |
| 05. | Temperature | : | 300 c to -200 c |
| 06. | Length of Penstock (Main) | : | 55 m |
| 07. 08 09 | Dia of Penstock (Main) Length of Branch Pipe Dia of Branch Pipe | : | 0.66m N/A N/A |
| 10. | Capacity | : | 1x230 KW |
| 11. | No. of Unit | : | 01 Units |
| 12. | Firm Capacity the unit | : | 230 KW |
| 11. | Net Head | : | 33 m |
| 12. | Design discharge/unit | : | 0.845 m3/sec |
| 13. | Type of turbine | : | Francis |
| 14. | Efficiency of Turbine | : | 92% |
| 15. | Rated Speed | : | 750 RPM |
| 16 17 18 . 19. | Runway speed Rotation Braking system Running | : | As Per design Clockwise seen from Generator side. Both electrical and pneumatic braking system may be provided to stop quickly the hydro generator to bring the turbine at standstill. Continuous. |
| 20 21 | Overall efficiency of unit Power Factor | : | 85% 0.8 Lagging |
| 22. 23 | Shaft Arrangement Direction of Rotation | : | Horizontal Clock wise seen form generator end. |
| 24. | Type of valve | : | Butterfly valve |
| 25. | Type of Governor | : | Flow and speed regulation based on load variation with PLC/PID Controlled Speed Governor. PLC equipped with PC HMI & hydraulic power pack with nitrogen filled cylinder and with arrangement for black start stability and droop characteristics suitable for isolated off grid operation. |
| 26 | Type of generator | : | Synchronous |
| 27. | Generation voltage | : | 0.4-0.440 KV |
| 29 | Efficiency of generator | : | 95% |
| 30. | Coupling mode | : | Directly coupled with horizontal turbine |
| 31. | Power factor | : | 0.80 |
| 32. | Connection of starter winding | : | Y |
| 33. | Frequency | : | 50 Hz |
| 34. | No. of Phased | : | 03 Phase |
| 35. | Type of excitation | : | Self-excitation (Brushless) |
| 36. | Insulation classes | : | F for stator, rotor and exciter |
| 37. | Mode of operation | : | Suitable for parallel operation and also with nearby power houses |
| 38. | Panel Board | : | All protective devices such as Low voltage air circuit breaker equipped with over/under voltage relays, over current, excitation, oil pressure, over speed, reverse power relays output voltage 415 volts, 3 phase at incoming, having capacity of 500 Amps. Motorized VCB (ABB-Italy) 630 Amps, rated voltage 12 KV, withdrawable type, operating voltage 11KV, 25KA. Bil 36/95 KV, shunt coil open and close (110vdc), motor mechanism (220 vac), digital Over Current, Earth fault & Short Circuit Protection Relay (ABB Model rex-610), energy meter (Bluestar) including all other accessories enclosed in metal clade steel panel, complete in all respect. Including all necessary meters such as Amp, Voltage, KW, KWh (digital), Power factor and frequency. Supply & fixing of all voltage grade power cables from generator to panel board and step up transformer, internal connections i.e. earthling set, auxiliary transformer. Sheets of heavy duty zinc plates for fabrication of cubical panels having easy opening and closing mechanism and should be placed on galvanized angle iron of requires thickness. |
| 39. 40 | Cable and wire THERMAL REQUIREMENTS: | : | All cables and wires for panel boards connections, control wiring and power cable of appropriate size in between Generator to panel board and from panel board to step-up transformers are laydown through cable tray and all bus bars should be copper strip of required capacity. The project is located at high altitude and temperatures varies from 30 degree to minus 20 Celsius. Therefore, a heater is required for governor oil. |

SCHEDULE – B TO BID

WORK TO BE PERFORMED BY SUBCONTRACTORS

The bidder shall do the work with his own forces.  Sub - contracting is not allowed.

SCHEDULE – C TO BID

PROPOSED PROGRAMME OF WORKS

Bidder shall provide a programme in a bar-chart/CPM/PERT form showing the sequence of work items by which he proposes to complete the work of the entire Contract. The programme should indicate the sequence of work items and the period of time during which he proposes to complete the Works including the activities like designing, schedule of submittal of drawings, ordering and procurement of materials, manufacturing, delivering, construction of civil works, erection, testing and commissioning of Works to be supplied under the Contract.

SCHEDULE – D TO BID

DEVIATIONS

FROM

TECHNICAL PROVISIONS

It is presumed that the bidder shall not take any deviation. However, if he intends to take deviations to the specified terms, those must be listed in the space provided below:

Sr. No.			Clause No. / Section No.		Deviations/Clarifications

[Note:	Attach additional sheets, if necessary]

SCHEDULE – E TO BID

DEVIATIONS

FROM

CONTRACTUAL CONDITIONS

It is presumed that the bidder shall not take any deviation. However, if he intends to take deviations to the specified Contractual/Commercial Conditions, those must be listed in the space provided below:

Sr. No.			Clause No. / Section No.		Deviations/Clarifications

[Note:	Attach additional sheets, if necessary]

SCHEDULE – F TO BID

METHOD OF PERFORMING WORKS

The bidder is required to submit a narrative outlining the method of performing the Works. The narrative should indicate in detail and include but not be limited to:

- The sequence and methods in which he proposes to carry out the Works, including the number of shifts per day and hours per shift, he expects to work.

- A list of all major items of constructional and erection plant, tools and vehicles proposed to be used in carrying out the Works at Site, including number of each kind, make, type, capacity of all equipment, working condition, which shall be deployed by him for Civil Work and Erection, Testing and Commissioning of the Works, in sufficient detail to demonstrate fully that the equipment will meet all the requirements of the Technical Provisions.

- The procedure for installation of equipment and transportation of equipment and materials to the site.

- Details regarding mobilization in Pakistan, the type of facilities including personnel accommodation, office accommodation, provision for maintenance and for storage, communications, security and other services to be used.

- Organization chart indicating head office & field office personnel involved in management, supervision and engineering of the Works to be done under the Contract.

SCHEDULE – G TO BID

PROPOSED ORGANISATION

The bidder shall list in this Schedule the key personnel he will employ from Head office and from Site office to direct and execute the Works, together with their names, qualifications, experience, positions held and their nationalities.

Summary of Qualifications

Designation		Name of		Experience, Present

Position and

Nationality

- Head Office:

- Site Office:

Contractor’s Representative

Site Superintendent

Supervising Engineer

Plant Erectors

Construction Supervisors

Other Key Staff

SCHEDULE – H TO BID

(INTEGRITY PACT)

DECLARATION OF FEES, COMMISSION AND BROKERAGE ETC.

PAYABLE BY THE SUPPLIERS OF GOODS, SERVICES & WORKS IN

CONTRACTS WORTH RS. 10.00 MILLION OR MORE

Contract No.________________ Dated __________________

Contract Value: ________________

Contract Title: _________________

………………………………… [name of Supplier] hereby declares that it has not obtained or induced the procurement of any contract, right, interest, privilege or other obligation or benefit from Government of Pakistan (GoP) or any administrative subdivision or agency thereof or any other entity owned or controlled by GoP through any corrupt business practice.

Without limiting the generality of the foregoing, [name of Supplier] represents and warrants that it has fully declared the brokerage, commission, fees etc. paid or payable to anyone and not given or agreed to give and shall not give or agree to give to anyone within or outside Pakistan either directly or indirectly through any natural or juridical person, including its affiliate, agent, associate, broker, consultant, director, promoter, shareholder, sponsor or subsidiary, any commission, gratification, bribe, finder’s fee or kickback, whether described as consultation fee or otherwise, with the object of obtaining or inducing the procurement of a contract, right, interest, privilege or other obligation or benefit in whatsoever form from GoP, except that which has been expressly declared pursuant hereto.

[name of Supplier] certifies that it has made and will make full disclosure of all agreements and arrangements with all persons in respect of or related to the transaction with GoP and has not taken any action or will not take any action to circumvent the above declaration, representation or warranty.

[name of Supplier] accepts full responsibility and strict liability for making any false declaration, not making full disclosure, misrepresenting facts or taking any action likely to defeat the purpose of this declaration, representation and warranty. It agrees that any contract, right, interest, privilege or other obligation or benefit obtained or procured as aforesaid shall, without prejudice to any other rights and remedies available to GoP under any law, contract or other instrument, be voidable at the option of GoP.

Notwithstanding any rights and remedies exercised by GoP in this regard, [name of Supplier] agrees to indemnify GoP for any loss or damage incurred by it on account of its corrupt business practices and further pay compensation to GoP in an amount equivalent to ten time the sum of any commission, gratification, bribe, finder’s fee or kickback given by [name of Supplier] as aforesaid for the purpose of obtaining or inducing the procurement of any contract, right, interest, privilege or other obligation or benefit in whatsoever form from GoP.

Name of Buyer: ………………		Name of Seller/Supplier: …………

Signature: ……………………		Signature: …………………………

[Seal]						[Seal]

# SCHEDULE OF PRICES

Description	Page No.

- Preamble to Schedule of Prices	48-56

- Schedule of Prices	57

2. (a)	Summary of Bid Prices

2. (b)	Equipment, Erection, Testing & 
		Commissioning

2. (c)	Civil Works

2. (d)	Daywork

2. (e)	Additional Recommended Erection and 
	Testing Equipment & Maintenance Tools

2. (f)	Additional Recommended Spare Parts

1. PREAMBLE TO SCHEDULE OF PRICES

1.	General

1.1	The Schedule of Prices shall be read in conjunction with the Conditions of Contract together with the Specifications.

1.2	The Contract shall be for the whole of the Works as described in these Bidding Documents. Bids must be for the complete scope of Work.

2.	Description

2.1	The general directions and descriptions of work and materials are not necessarily repeated nor summarized in the Schedule of Prices. References to the relevant sections of the Bidding Documents shall be made before entering prices against each item in the Schedule of Prices.

2.2	The quantities shown in the Schedule of Prices are estimated quantities only as an indication of the Scope of Work to enable the bidder to bid for different items of the Works for his estimate of costs. The estimated quantities shall be used for comparing the bids. It is, however, to be noted that in the event of any increase or decrease in the quantity of any item of Works and subject to provisions of the Conditions of Contract herein, the actual quantities executed will be paid.

3.	Units & Abbreviations

3.1	Units of measurement, symbols and abbreviations expressed in the Bidding Documents shall comply with the System International Unit (SI Units).

The following abbreviations shall be used in the Schedule of Prices:

Abbreviation

Number						No.

Kilometer						km

Kilogram						Kg				Cubic Meter						m3

Provisional Sum					PS

Percent 						%

Mega Watt						MW

Kilo Watt						KW

Above mean sea level				AMSL

Meter							m

Milli meter						mm

4.	Rates and Prices

4.1	Except as otherwise expressly provided under the Conditions of Contract, the rates and amounts entered in the Schedule of Prices shall be the rates at which the Contractor shall be paid and shall be the full inclusive value of the work set forth or implied in the Contract; except for the amounts reimbursable to the Contractor under the Contract.

4.2	Unless otherwise stipulated in the Conditions of Contract, the rates and prices entered by the bidder shall not be subject to adjustment during the performance of the Contract.

4.3	All duties, taxes and other levies payable by the Contractor under the Contract, or for any other cause, as on the date twenty-eight (28) days prior to the deadline for submission of bids shall be included in the rates and prices and the total Bid Price submitted by a bidder.

Additional/reduced duties, taxes and levies due to subsequent additions or changes in legislation shall be reimbursed/deducted as per provisions of the Conditions of Contract.

4.4	The whole cost of complying with the provisions of the Contract shall be included in the items provided in the priced Schedule of Prices, and where no items are provided, the cost shall be deemed to be distributed among the rates and prices entered for the related items of the Works and no separate payment will be made for those items.

The rates, prices and amounts shall be entered against each item in the Schedule of Prices. Any item against which no rate or price is entered by the bidder will not be paid for by the Employer when executed and shall be deemed covered by the rates and prices for other items in the Schedule of Prices.

4.5	The bidder shall be deemed to have obtained all information as to port clearance facilities and charges, loading and unloading facilities and charges, storage facilities and charges, transportation facilities and charges, congestion and/or other conditions to be expected at Karachi Port and or any other seaport/ boarder of Pakistan and all requirements related thereto.

The Contractor shall be responsible to make complete arrangements for the transportation of the Plant to the Site.

The bidder shall be deemed to have included all clearing, forwarding and other incidental costs in this regard in his bid. The Contractor will have the option to use either Karachi Port or any other seaport boarder of Pakistan.

4.6	The Contractor shall provide for all parts of the Works to be completed in every respect for commercial operation. Notwithstanding that any details, accessories, etc. required for the complete installation and satisfactory operation of the Plant, are not specifically mentioned in the Specifications, such details shall be considered as included in the Contract Price.

5.	Bid Prices

5.1	Break-up of Bid Prices

The various elements of Bid Prices shall be quoted as detailed below:

a)	FOB Port of Shipment

The bidder shall quote prices for FOB Port of Shipment for all individual items and for each sub-total of Plant, Erection Equipment and Spare Parts to be supplied from outside Pakistan on FOB (Port of Shipment) basis. The FOB Port of Shipment price shall include the cost of the following:

i)	Design, manufacture, finishing, factory testing, packing for transport and all transportation costs incurred in placing the Plant, Erection Equipment and Spare Parts and other materials on board the vessel.

ii)	Provision of clean on-board bills of lading.

iii)	Export taxes, fees or charges levied on exporting Plant, Erection Equipment and Spare Parts and other materials in the country of origin, in the case of Plant imported to Pakistan.

iv)	Provision of certificates of origin, consular invoices (if required) or any other documents issued in the country of origin.

b)	Insurance & Shipping

i)	Insurance

The bidder shall quote prices for insurance cover from ex-factory/ ex-works to the Site for the sub-totals of the Plant, Erection Equipment, Spare Parts and other materials to be imported for the Contract. Such prices shall include all insurance costs covering the responsibility for all loss or damages while loading, unloading, storing and trimming on board or on inland carrier and transportation to Site.

The prices for transportation/marine insurance cover shall be quoted on the basis of insurance through insurers from any country(ies) of the world acceptable to the Employer.

ii)	Shipping

The bidder shall quote prices for shipping from port of shipment to the port of entry in Pakistan for the sub-totals of the Plant, Erection Equipment, Spare Parts and other materials to be imported for the Contract in Pakistan. Such prices shall include all marine transportation costs including ocean freight and other charges, etc.

The prices for shipping/marine transportation shall be quoted for shipment through reputed shipping lines including Pakistan National Shipping Corporation (PNSC).

Cost of shipment(s) effected by the Contractor at his option by aircraft shall be deemed to be included in the Total Bid Price.

c)	CIF (Pakistan Seaport) Price

CIF (Pakistan Seaports) price will be the total of FOB price, insurance and shipping prices, described here above.

d)	Customs Duties

Customs duty for Plant, Erection Equipment, Spare Parts and other materials, if any, offered from outside Pakistan shall also include sales tax, import duty and other import charges.

e)	DDP (Pakistan Seaport) Price

DDP (Pakistan Seaport) price will be the total of CIF price and customs duties, described here above.

f)	Ex-factory Price for Local Goods

The bidder shall quote prices for Local Goods, materials (other than materials required for civil works such as concrete and reinforcement etc. Cost of which will be included in the price of civil works) and equipment in the relevant column of Ex-Factory (Pakistan) of “Schedule of Prices”. Such prices shall include:

i)	Design documentation, drawings, drafting, planning services, manufacturing, testing and packing of finished goods ready for delivery to Site.

ii)	All custom duties, sales tax and other taxes already paid or payable on the components and raw materials used in the manufacture or assembly of Local Goods, materials and equipment.

g)		Insurance of Local Goods

Insurance of Local Goods and other materials from factory to Site shall include all insurance costs covering the responsibility of all losses or damages, while loading, unloading, storing, trimming on the carrier and transporting to Site. Checking and verifying of consignments, issuance of receiving reports and damage reports (when applicable) shall be the Contractor’s responsibility.

h)	Local Transport

Inland transportation for the Plant, Erection Equipment and Spare Parts shall be the Contractor’s responsibility in respect of:

i)	the Plant, Erection Equipment, Spare Parts and other materials offered from outside Pakistan; from the port of entry in Pakistan to the storage area at the Site, and

ii)	indigenous Plant, Erection Equipment, Spare Parts and other materials if any, offered from within Pakistan; from the factory in Pakistan to the storage area at the Site, and

all charges occurring therefrom including octroi, zila tax, fees etc. and charges for loading, forwarding and unloading expenses shall be borne by the Contractor. Unloading at the Site, handling of the Plant, Erection Equipment, Spare Parts and other materials to the designated point of Site storage, checking and verifying all shipments received against shipping documents, issue of all receiving reports and issues of damage reports (when applicable) shall be the Contractor’s responsibility.

The bidder shall recognize such elements of the costs which he expects to incur in the performance of the Works and shall include all such costs in the rates and amounts entered in the Schedule of Prices.

i)	Erection & Other Work

The bidder shall quote prices for Erection & Other Work (foreign and local currency portion) for the sub-totals of the Plant at the Site. Such prices shall include the costs of handling of the Plant and other materials from Site storage to point of final installation, erection, installation, testing, commissioning including all inspection, reliability tests, the cost of foreign and local erection staff and labor, tools and equipment, etc. It shall also cover the services of qualified representative(s) of the supplier(s) of Plant or adviser(s) to assure proper erection and commissioning of the Plant. The price shall also include cost of arranging insurances in respect of Contractor’s operations in Pakistan which insurances shall be effected by the Contractor with the National Insurance Company (NIC) of Pakistan or any other insurance company operating in Pakistan and acceptable to the Employer.

5.2	Total Bid Price

The total of bid prices under foreign currency shall be entered in the Summary of Bid Prices. The unit rates and prices and lump sum amount entered in the Schedule of Prices will be the rates at which the Contractor will be paid in PKR at the exchange rate as declared under the prescribed rule, and shall be deemed to be the full inclusive value of the work including all costs of performing the Works such as overheads, income tax, super tax, profits, costs of accepting the general risks, liabilities and obligations set forth or implied in the Contract except for the amounts reimbursable, if any, to the Contractor under the Contract. The rates shall also include Contractor’s cost for providing Performance Security and other Bank Guarantees required for performance of the Contract.

6.	Erection and Testing Equipment and Maintenance Tools

6.1	In the Schedule of Prices, under Erection and Testing Equipment & maintenance tools the Employer has drawn up a list of Erection and Testing Equipment and Maintenance Tools along with estimated quantities. The bidder shall enter the price only in FOB price column for all individual items and shall give the break-up of the prices into FOB Port of Shipment, Shipping to wharf at the port of entry in Pakistan, Insurance to Site and Local Transport in Pakistan against each sub-total. These Erection and Testing Equipment and Maintenance Tools shall be furnished and the cost included in the Bid Price.

The Employer shall have the option of ordering additional quantities of these essential Erection and Testing Equipment and Maintenance Tools, at the unit rates entered in the Schedule of Prices no later than one year after the Commencement Date.

The unit rate for any item shall be computed by dividing the total amount by the quantity of that item.

6.2	The bidder shall also list, in the space provided in the Schedule of Prices, Additional Recommended Erection and Testing Equipment and Maintenance Tools, any Erection and Testing Equipment and Maintenance Tools which he recommends be provided for the Works, in addition to those already specified by the Employer in the Schedule of Prices. The bidder shall enter against each such item, its recommended quantity, and price. The cost of such Additional Recommended Erection and Testing Equipment and Maintenance Tools will not be taken into account in the evaluation of bids.

The Additional Recommended Erection and Testing Equipment and Maintenance Tools may be selected by the Engineer/Employer and the Contract Price will be adjusted in accordance with the prices set against those items in the Schedule of Prices.

7.	Spare Parts

7.1	In the Schedule of Prices, under Spare Parts, the Employer has drawn up a list of spare parts along with estimated quantities. The bidder shall enter the price only in FOB price column for all individual items and shall indicate the break-up of price into FOB Port of Shipment, Shipping to wharf at the port of entry in Pakistan, Insurance to Site and Local Transport in Pakistan against each sub-total. These spare parts shall be furnished and the cost included in the Bid Price.

The successful Bidder shall prepare and at the time of preparation of Letter of Acceptance submit to the Employer the unit rates of all individual items of the spare parts. The unit rates of the spare parts for the required quantities shall give a total cost equal to the amount entered in the Schedule of Price for spare parts.

The Employer shall have the option of ordering additional quantities of these essential spare parts, at the unit rates entered in the Schedule of Prices, no later than one year after the Commencement Date.

The unit rate for any item shall be computed by dividing the total amount by the quantity of that item.

7.2	The Bidder shall also list in the space provided in the Schedule of Prices any Spare Parts which he recommends be provided for the Works, in addition to those specified by the Employer in the Schedule of Prices. The Bidder shall enter against each such item, its recommended quantity, rate and price. The cost of such Additional Recommended Spare Parts will not be considered in the evaluation of bids.

The Additional Recommended Spare Parts may be selected by the Engineer/ Employer and the Contract Price will be adjusted in accordance with the prices set against those items in the Schedule of Prices.

8.	Reimbursable Costs

8.1	If provided in the Particular Conditions of Contract, the Contractor shall be reimbursed the actual amounts (without any overhead charges and profits) disbursed by him in respect of non-exempt Pakistani customs, import duties, and taxes, levied upon Plant, Erection Equipment and Spare Parts imported directly by him or his subcontractors into Pakistan for the purpose of this Contract for incorporation in the Works.

8.2	The bidder shall recognize such elements of the costs which he expects to incur in the performance of the Works and which are reimbursable, and he shall not include any such costs in the rates and amounts entered in the Schedule of Prices.

9.	Provisional Sums

9.1	Provisional Sums included and so designated in the Schedule of Prices if any, shall be expended in whole or in part at the direction and discretion of the Employer/ Engineer. The Contractor will only receive payment in respect of Provisional Sums if he has been instructed by the Employer/Engineer to utilize such sums.

DAYWORK SCHEDULE

1.	General

1.1	Work shall not be executed on a Day work basis except by written Order of the Employer. The rates for Day work items entered in the Schedule of Prices shall apply to any quantity of Day work ordered by the Engineer. Nominal quantities have been indicated against each item of Day work, and the extended total for Day work shall be carried forward as a provisional sum to the Summary of Bid Prices.

2.	Day work - Labor

2.1	In calculating payments due to the Contractor for the execution of Day work, the hours for labor shall be reckoned from the time of arrival of the labor at the job Site to execute the particular item of Day work to the time of departure, but excluding meal breaks and rest periods. Only the times of classes of labor directly doing work ordered by the Engineer and for which they are competent to perform shall be measured.

The time of Plant Erectors or other expatriate supervisory personnel shall not be measured unless their time on Site is extended by Variation Order. The rates entered by the Bidder for these categories shall be daily rates inclusive of all allowances and overheads.

2.2	For labor other than Plant Erectors or other expatriate supervisory personnel, the Contractor shall be entitled to payment in respect of the total time that labor is employed on Day work, calculated at the basic rates entered by him in the Schedule of “Day work Rates – Labor” together with an additional percentage payment on basic rates representing the Contractor's profit, overheads, etc., as described below:

a)	The basic rates for labor shall cover all direct costs to the Contractor, including (but not limited to) the amount of wages paid to such labor, transportation time, overtime, subsistence allowances and any sums paid to or on behalf of such labor for social benefits in accordance with Pakistan Labor laws. The basic rates will be payable in Pak. Rupees only, and

b)	The additional percentage payment to be quoted by the Bidder and applied to costs shall be deemed to cover the Contractor's overheads, profits, superintendence, liabilities and insurances and allowances to labor, timekeeping and clerical and office work, the use of consumable stores, water, lighting and power; the use and repair of staging, scaffolding, workshops and stores, portable power tools, manual plant and tools; supervision by the Contractor's staff, foremen and other supervisory personnel; and charges incidental to the foregoing. Payments under this item shall be made in foreign currency and local currency at the percentages entered in the Day work Schedule.

2.3	Rates entered in the Day work Schedule shall apply to labor of trade and qualification as described and to labor of other trades with similar skill and qualification.

3.	Day work - Contractor's Equipment

3.1	The Contractor shall be entitled to payments in respect of Contractor's Equipment already on Site and employed on Day work at the basic rental rates entered by him in the "Schedule of Day work Rate - Contractor's Equipment". The said rates shall be deemed to include complete allowance. For depreciation, interest, indemnity and insurance, repairs, maintenance, supplies, fuel, lubricants and other consumables and all overheads, profit and administrative costs related to the use of such equipment.

3.2	In calculating the payment due to the Contractor for Contractor's Equipment employed on Day work, only the actual number of working hours will be eligible for payment, except that, where applicable and agreed with the Engineer, the travelling time from the part of the Site where the Contractor's Equipment was located when ordered by the Engineer to be employed on Day work and the time for the return journey thereto shall be included for payment.

3.3	The rental rates for Contractor's Equipment employed on Day work shall be stated in Pakistani Rupees but payments to the Contractor will be made in local and foreign currencies according to the rates entered in the Schedule.

4.	Day Work-Materials

4.1	The Contractor shall be entitled to the following payments in respect of materials used for Day work (except for materials for which the cost is included in the percentage addition to labor costs) which are actually incorporated into the Works:

a)	The net cost of such materials delivered to warehouse or work yard area or storage area at the Site. Such cost shall be calculated by the Contractor on the basis of the invoiced price and freight and insurance as certified by the Engineer on the basis of invoices produced.

b)	Percentage addition, in local and/or foreign currency, of such net cost of materials to cover the Contractor's handling charges, overheads and profits.

4.2	Payment of the net cost to the Contractor of Day work materials shall be made in the same currency as the invoice. Payment of the addition for handling charges, overheads and profit shall be in local and/or foreign currency as entered in the Schedule of Day work - Materials.

2. (a) SCHEDULE OF PRICES – SUMMARY OF BID PRICES

All prices must be according to SCHEDULE-A TO BID

| Item No. | Description | Qty | Price per Unit (PKR) in figures | Total price (PKR) |  |  | TOTAL PRICE (words) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2 (a) | Main Plant (1x230KW) Including the following components - Inlet valve, - Discharge/Dewatering valve - Reducer - Expansion joint - Francis Turbine, - Generator, - Governor - Control panel boards. - Incoming circuit breakers, - Protective relays - Measuring instruments, - Outgoing circuit breaker, necessary cables, wires and auxiliary items complete in all respect. | 1 Set |  |  |  |  |  |
| i. | Main plants CIF Cost. |  |  |  |  |  |  |
| Ii | Clearance from Port. |  |  |  |  |  |  |
| iii. | Local transportation, commissioning & test running. |  |  |  |  |  |  |
| iv. | Spare parts CIF Cost |  |  |  |  |  |  |
| v. | Clearance from Port |  |  |  |  |  |  |
| vi. | Local transportation |  |  |  |  |  |  |
| vii. | Tools CIF Cost |  |  |  |  |  |  |
| viii. | Clearance from Port |  |  |  |  |  |  |
| ix. | Local transportation |  |  |  |  |  |  |
| X | Six-month O&M |  |  |  |  |  |  |
| Xi | FAT at manufacturing facility before Shipment |  |  |  |  |  |  |
|  | Total Price |  |  |  |  |  |  |

(Note: Total Price, shall be provided in figures as well as in words.

2. (b) SCHEDULE OF PRICES – EQUIPMENT,

ERECTION, TESTING & COMMISSIONING

|  |  |  |  |  | Imported Goods |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item No. | Description | Unit | Qty | FOB Price |  | Shipping | Insurance | CIF Pak Sea Port | Custom duties if any | Local Trans- portation | Erection & Other Work | Total Cost Rs |
| 1 | 2 | 3 | 4 | 5 |  | 6 | 7 | 8 |  |  | 9 | 10 |
| 1. | Main plant | Sets | 2 |  |  |  |  |  |  |  |  |  |
| 2 | Spare Parts |  |  |  |  |  |  |  |  |  |  |  |
| 3 | Tools |  |  |  |  |  |  |  |  |  |  |  |
|  | Total cost |  |  |  |  |  |  |  |  |  |  |  |

red in Pakistan shall also fill Appendix C to Instructions to Bidders.]

- (c) SCHEDULE OF PRICES – CIVIL WORKS

Not Required

| Item No. | Description | Unit | Qty | Volume of Concrete per Foundation (m3) | Weight of Steel per Foundation (kg) | Unit Rate of Concrete per m3 (PKR) | Unit Rate of Steel per kg (PKR) | Unit Rate per Foundation (PKR) | Total (PKR) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | NOT APPLICABLE |  |  |  | DELETED |  |  |  |  |
| Total (to be carried to Summary of Bid Price) |  |  |  |  |  |  |  |  |  |  |  |

2. (d) SCHEDULE OF PRICES

DAYWORK – Not Required

| Item No. | Description | Nominal Quantity | UNIT RATE |  | TOTAL AMOUNT |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | DELETED | FCC | LCC (PKR) | FCC | LCC (PKR) |
| 1. 2. 3. | Day work-Labor Day work - Contractor’s Equipment Day work – Materials |  |  |  |  |  |
| Total (to be carried to Summary of Bid Price) |  |  |  |  |  |  |  |

2. (e) SCHEDULE OF PRICES – ADDITIONAL

RECOMMENDED ERECTION AND TESTING EQUIPMENT &

MAINTENANCE TOOLS

- The bidder shall propose in the space provided, a detailed list of Erection and Testing Equipment & Maintenance Tools which are recommended by him in addition to those specified by the Employer under Schedule 2(b) above.

- The purchase of additional recommended Erection and Testing Equipment & Maintenance Tools would be at the discretion of the Employer and the cost of such equipment will not be taken into consideration in the evaluation of bids. However, the Contract Price will be adjusted to include the cost of additional Erection and Testing Equipment & Maintenance Tools which are selected by the Employer.

- The list of Erection and Testing Equipment & Maintenance Tools shall include description as well as quantity of each item and the unit rate and prices for the total quantity proposed for each item of Erection and Testing Equipment & Maintenance Tools.

| Item No. | Description | Unit | Qty | Unit Rate |  |  |  |  |  |  |  |  | Total Price |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Foreign Currency Component |  |  |  |  | Local Currency Component |  |  |  | Foreign Currency Component | Local Currency Component |
|  |  |  |  | FOB Price | Shipping | Insurance | CIF Pak Sea Port | Total | Customs Duty for Col No.8 | ExFac-tory Pakistan (For Local Goods) | Local Trans- port | Total |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |
| 1. 2. 3. | Erection Equipment Testing Equipment Maintenance Tools |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total (not to be carried to Summary of Bid Price) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

2. (f) SCHEDULE OF PRICES – ADDITIONAL

RECOMMENDED SPARE PARTS

- The bidder shall propose in the space provided, a detailed list of Spare Parts which are recommended by him in addition to those specified by the Employer under Schedule 2(b) above.

- The purchase of additional recommended Spare Parts would be at the discretion of the Employer and the cost of such equipment will not be taken into consideration in the evaluation of bids. However, the Contract Price will be adjusted to include the cost of additional Spare Parts which are selected by the Employer.

- The list of Spare Parts shall include description as well as quantity of each item and the unit rate and prices for the total quantity proposed for each item of Spare Parts.

| Item No. | Description | Unit | Qty | Unit Rate |  |  |  |  |  |  |  |  | Total Price |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Foreign Currency Component |  |  |  |  | Local Currency Component |  |  |  | Foreign Currency Component | Local Currency Component |
|  |  |  |  | FOB Price | Shipping | Insurance | CIF Pak Sea Port | Total | Customs Duty for Col No.8 | Ex-Factory Pakistan (For Local Goods) | Local Trans- port | Total |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |
| Total (not to be carried to Summary of Bid Price) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

PREAMBLE

TO

CONDITIONS OF CONTRACT

|  | PREAMBLE TO CONDITIONS OF CONTRACT |
| --- | --- |
|  | [This Preamble must be completed before issuance of Bidding Documents and shall contain essential requirements of General Conditions of Contract & Particular Conditions of Contract.] |
| Commencement Date | Sub-Clause 1.1.1.(i) The date for commencement of the Works is the date of signing of contract |
| Defect Liability Period | Sub-Clause 1.1.11 The Defect Liability Period is 365 days. |
| The Employer | Sub-Clause 1.1.12. The Employer is Aga khan Rural Supports Programme (AKRSP) |
| The Engineer | Sub-Clause 1.1.15. The Engineer is Engineers of AKRSP |
| Time for Completion | Sub-Clause 1.1.35. The Time for Completion is 300 Days from the Commencement Date. |
| Warranty Period | Sub-Clause 1.1.40. The Warranty Period is 01 years for (goods/equipment) |
| Engineer’s Duties & Authorities | Sub-Clause 2.1 Amount of Variation Order in emergency is 15% |
| Confirmation in Writing | Sub-Clause 2.6 (i) If the Contractor shall require the confirmation it shall be notified to the Employer within 30 days. (ii) Employer shall confirm the decision/instruction within 30 days. |
| Ruling Language | Sub-Clause 5.1. The version in English language (ruling language) shall prevail. |
| Day to Day Communications | Sub-Clause 5.2. The language for day to day communications is English. |
| As-Built Drawings | Sub-Clause 6.10 As-Built drawings shall be provided to the Employer within 30 days from the date of issue of Taking Over Certificate. |
| General Obligations | Sub-Clause 8.1 Detail of Erection and Testing Equipment and Maintenance Tools is given herein below: Attached (SP-12 & 13) |
| Programme to be Furnished | Sub-Clause 12.1. The Programme must be submitted in the form of written request. |
| Electricity Water, Gas and Other Services | Sub-Clause 14.3. Supplies on the Site are: a. Electricity: To be arrange by the contractor b. Water to be arrange by the contractor c. Gas LPG will be arranged by the contractor. d. Other Services will be responsibility of contractor |
| Employer’s Equipment | Sub-Clause 14.4. There is no Employer’s equipment, available for use by the Contractor. |
| Working Hours | Sub-Clause 18.3. The normal working hours will be according to office timings notified by the Government. |
| Time for Completion | Sub-Clause 25.1 (i) Place of the Project site is mentioned in the bid document (ii) Period (300 days) |
| Earlier Completion | Sub-Clause 26.3 (i) Amount of Bonus per day Nil (ii) Max. Amount of Bonus Nil |
| Delay in Completion | Sub-Clause 27.1. Failure to meet the Time for Completion entitles the Employer to reduction in Contract Price as follows: Percentage per day 0.05 % Maximum 10 % |
| Prolonged Delay | Sub-Clause 27.2. Maximum amount recoverable from the Contractor by the Employer 20% |
| Terms of Payment | Sub-Clause 33.1. In addition to the provisions under Clause 33, the terms of payment shall be as stated in Particular Conditions of Contract. |
| Payment | Sub-Clause 33.5 (i) Period of Payment by Employer to Contractor 45 days. (ii) Period of Final Certificate of Payment 06 Months after the completion of the work. |
| Payment in Foreign Currencies | Sub-Clause 35.1. Payment in foreign currencies shall be arranged as follows: PKR |
| Insurance of Works | Sub-Clause 43.1. The deductible limits in the insurance cover of the Works shall not exceed 02% Sub-Clause 43.1.(a) The additional risks to be insured are: Transportation of equipment up to the site, laborer during transportation, loading/unloading, installation, commissioning & test running. |
| Third Party Liability | Sub-Clause 43.3. The amount of insurance against third party liability taken out by the Contractor shall not be less than: 1% |
| Payment on Termination for Employer’s Default | Sub-Clause 46.3. The additional amount payable by the Employer on termination shall not exceed: The value of work done assessed by the committee constituted by the employer. |
| Labour, Materials and Transport | Sub-Clause 47.1. The method of calculating adjustments for changes in costs shall be: No price escalation shall be paid being imported goods |
| Notices to Employer and Engineer | Sub-Clause 49.2. The address of the Employer for notices is: - AKRSP core office Babar Road Kashrote Gilgit |
| Disputes & Arbitration | Sub-Clause 50.4 Venue of Arbitration District Upper Chitral Khyber Pakhtunkhwa. |
| Applicable Law | Sub-Clause 51.1. The applicable law is the Civil law of Pakistan |
| Procedural Law for Arbitration | Sub-Clause 51.2. The procedural law for arbitration is the Civil Law of Pakistan |
| Language and Place of Arbitration | Sub-Clause 51.3. The language of arbitration is English/urdu languages. The place of arbitration is District Upper Chitral Khyber Pakhtunkhwa. |

GENERAL CONDITIONS OF CONTRACT

[Notes on the Conditions of Contract

The Conditions of Contract comprise two parts:

(a)	General Conditions of Contract

(b)	Particular Conditions of Contract

Over the years, a number of “model” General Conditions of Contract have evolved. The one used in these Standard Bidding Documents was prepared by the International Federation of Consulting Engineers (Federation Internationale des Ingenieurs-Conseils, or FIDIC), and is commonly known as the FIDIC Conditions of Contract. (The used version is the 1987 edition, reprinted in 1988 with editorial amendments.)

The FIDIC Conditions of Contract have been prepared for an ad measurement (unit price or unit rate) type of contract, and cannot be used without major modifications for other types of contract, such as lump sum, turnkey, or target cost contracts.

The standard text of the General Conditions of Contract chosen must be retained intact to facilitate its reading and interpretation by bidders and its review by the Employer. Any amendments and additions to the General Conditions, specific to the contract in hand, should be introduced in the Particular Conditions of Contract.

The use of standard conditions of contract for all electrical/mechanical Works will ensure comprehensiveness of coverage, better balance of rights or obligations between Employer and Contractor, general acceptability of its provisions, and savings in time and cost for bid preparation and review, leading to more economic prices.

The FIDIC Conditions of Contract are copyrighted and may not be copied, faxed, or reproduced. Without taking any responsibility of its being accurate, Pakistan Engineering Council with prior consent of FIDIC Secretariat, has reproduced herein the FIDIC General Conditions of Contract for reference purpose only which cannot be used by the users for preparing their bidding documents. The bidding document may include a purchased copy, the cost of which can be retrieved as part of the selling price of the bidding document. Alternatively, the FIDIC Conditions of Contract can be referred to in the bidding documents, and the bidders are advised to obtain copies directly from FIDIC.*

* Add the following text if the bidding documents, as issued, do not include a copy:

“Copies of the FIDIC Conditions of Contract can be obtained from:

FIDIC Secretariat

P.O. Box 86

1000 Lausanne 12

Switzerland

fidic.pub@fidic.org – FIDIC.org/bookshop]

FEDERATION INTERNATIONALE DES INGENIEURS-CONSEILS

CONDITIONS OF CONTRACT

FOR ELECTRICAL AND

MECHANICAL WORKS

INCLUDING ERECTION ON SITE

WITH FORMS OF TENDER AND AGREEMENT

THIRD EDITION 1987

Reprinted 1988 with editorial amendments

CONTENTS

PART I: GENERAL CONDITIONS

Definitions and Interpretations

1.1	Definitions

1.2	Headings and Titles

1.3	Interpretation

1.4	Written Communications

1.5	Notice, Consents and Approvals

1.6	Cost, Overhead Charges and Profit

1.7	Periods

Engineer and Engineer’s Representative

2.1	Engineer’s Duties

2.2	Engineer’s Representative

2.3	Engineer’s Power to Delegate

2.4	Engineer to Act Impartially

2.5	Engineer’s Decisions and Instructions

2.6	Confirmation in Writing

2.7	Disputing Engineer’s Decisions and Instructions

2.8	Replacement of Engineer

Assignment and Subcontracting

3.1	Assignment

4.1	Subcontracting

Contract Documents

5.1	Ruling Language

5.2	Day to Day Communications

5.3	Priority of Contract Documents

5.4	Documents Mutually Explanatory

6.1	Contractor’s Drawings

6.2	Consequences of Disapproval of Contractor’s Drawings

6.3	Approved Contractor’s Drawings

6.4	Inspection of Contractor’s Drawings

6.5	Installation Information

6.6	Operation and Maintenance Manuals

6.7	Employer’s Use of Contractor’s Drawings

6.8	Contractor’s Use of Employer’s Drawings

6.9	Manufacturing Drawings

7.1	Errors in Contractor’s Drawings

7.2	Errors by Employer or Engineer

Obligations of the Contractor

8.1	General Obligations

8.2	Setting Out

9.1	Contract Agreement

10.1	Performance Security

10.2	Period of Validity

10.3	Claims under Performance Security

11.1	Site Data

11.2	Sufficiency of Contract Price

11.3	Physical Obstructions and Conditions

12.1	Programme to be Furnished

12.2	Alternation to Programme

12.3	Revision of Programme

13.1	Contractor’s Representative

13.2	Objection to Contractor’s Employees

14.1	Contractor’s Equipment

14.2	Safety Precautions

14.3	Electricity, Water and Gas

14.4	Employer’s Equipment

14.5	Clearance of Site

14.6	Opportunities for Other Contractors

14.7	Authority for Access

14.8	Information for Import Permits and Licences

15.1	Compliance with Statues, Regulations

15.2	Compliance with Laws

16.1	Patent Rights

16.2	Claims in respect of Patent Rights

16.3	Employer’s Warranty of Patent Rights

Obligations of the Employer

17.1	Access to and Possession of the Site

17.2	Assistance with Local Regulations

17.3	Civil Works on Site

17.4	Consents and Way leaves

17.5	Import Permits and Licences

Labor

18.1	Engagement of Labor

18.2	Returns of Labor

18.3	Working Hours

18.4	Restriction of Working Hours

Workmanship and Materials

19.1	Manner of Execution

19.2	Covering up Work

19.3	Uncovering Work

20.1	Independent Inspection

20.2	Inspection and Testing During Manufacture

20.3	Dates for Inspection and Testing

20.4	Facilities for Testing

20.5	Certificate of Testing

21.1	Rejection

22.1	Permission to Deliver

Suspension of Works, Delivery or Erection

23.1	Order to Suspend

24.1	Cost of Suspension

24.2	Payment in Event of Suspension

24.3	Prolonged Suspension

24.4	Resumption of Work

Completion

25.1	Time for Completion

26.1	Extension of Time for Completion

26.2	Delays by Subcontractors

26.3	Earlier Completion

27.1	Delay in Completion

27.2	Prolonged Delay

Tests on Completion

28.1	Notice of Tests

28.2	Time for Tests

28.3	Delayed Tests

28.4	Facilities for Tests on Completion

28.5	Retesting

28.6	Disagreement as to Result of Tests

28.7	Consequences of Failure to Pass Tests on Completion

28.8	Use by the Employer

28.9	Test Certificate

Taking Over

29.1	Taking-Over

29.2	Taking-Over Certificate

29.3	Use before Taking-Over

29.4	Interference with Tests on Completion

Defects after Taking Over

30.1	Defects Liability Period

30.2	Making Good Defects

30.3	Notice of Defects

30.4	Extension of Defects Liability Period

30.5	Failure to Remedy Defects

30.6	Removal of Defective Work

30.7	Further Tests on Completion

30.8	Right of Access

30.9	Defects in Employer’s and Engineer’s Designs

30.10	Contractor to Search

30.11	Defects Liability Certificate

30.12	Exclusive Remedies

Variations

31.1	Engineer’s Right to Vary

31.2	Variation Order Procedure

31.3	Disagreement on Adjustment of the Contract Price

31.4	Contractor to Proceed

31.5	Record of Costs

Ownership of Plant

32.1	Ownership of Plant

Certificates and Payment

33.1	Terms of Payment

33.2	Method of Application

33.3	Issue of Certificate of Payment

33.4	Corrections to Certificates of Payment

33.5	Payment

33.6	Delayed Payment

33.7	Remedies on Failure to Certify or Make Payment

33.8	Payment by Measurement

33.9	Application for Final Certificate of Payment

33.10	Issue of Final Certificate of Payment

33.11	Final Certificate of Payment Conclusive

Claims

34.1	Procedure

34.2	Assessment

Foreign Currency and Rates of Exchange

35.1	Payment in Foreign Currencies

35.2	Currency Restrictions

35.3	Rates of Exchange

Provisional Sums

36.1	Use of Provisional Sums

36.2	Ordering Work against Provisional Sums

36.3	Invoices and Receipts

36.4	Payment against Provisional Sums

Risks and Responsibility

37.1	Allocation of Risks and Responsibility

37.2	Employer’s Risks

37.3	Contractor’s Risks

Care of the Works and Passing of Risk

38.1	Contractor’s Responsibility for the Care of the Works

38.2	Risk Transfer Date

39.1	Passing of Risk of Loss or of Damage to the Works

39.2	Loss or Damage Before Risk Transfer Date

39.3	Loss or Damage After Risk Transfer Date

Damage to Property and Injury to Persons

40.1	Contractor’s Liability

40.2	Employer’s Liability

41.1	Accidents

Limitations of Liability

42.1	Liability for Indirect or Consequential Damage

42.2	Maximum Liability

42.3	Liability after Expiration of Defects Liability Period

42.4	Exclusive Remedies

42.5	Mitigation of Loss or Damage

42.6	Foreseen Damage

Insurance

43.1	The Works

43.2	Contractor’s Equipment

43.3	Third Party Liability

43.4	Employees

43.5	General Requirements of Insurance Policies

43.6	Permitted Exclusions from Insurance Policies

43.7	Remedies on the Contractor’s Failure to Insure

43.8	Amounts not recovered

Force Majeure

44.1	Definition of Force Majeure

44.2	Effect of Force Majeure

44.3	Notice of Occurrence

44.4	Performance to Continue

44.5	Additional Costs caused by Force Majeure

44.6	Damage caused by Force Majeure

44.7	Termination in Consequence of Force Majeure

44.8	Payment on Termination for Force Majeure

44.9	Release from Performance

44.10	Force Majeure Affecting Engineer’s Duties

Default

45.1	Notice of Default

45.2	Contractor’s Default

45.3	Valuation at Date of Termination

45.4	Payment after Termination

45.5	Effect on Liability for Delay

46.1	Employer’s Default

46.2	Removal of Contractor’s Equipment

46.3	Payment on Termination for Employer’s Default

Changes in Cost and Legislation

47.1	Labour, Materials and Transport

47.2	Statutory and Other Regulations

Customs

48.1	Customs and Import Duties

48.2	Clearance through Customs

Notices

49.1	Notice to Contractor

49.2	Notice to Employer and Engineer

49.3	Minutes of Meetings

Disputes and Arbitration

50.1	Disputes concerning Engineer’s Decisions

50.2	Arbitration

50.3	Works to Continue

50.4	Time Limit for Arbitration

Law and Procedure

51.1	Applicable Law

51.2	Procedural Law

51.3	Language

INDEX

PART-I: GENERAL CONDITIONS

Definitions and Interpretations

1.1	Definitions

In the Contract (as hereinafter defined) the following words and expressions shall have the meanings hereby assigned to them:

1.1.1	"Commencement Date" means which-ever is the latest of:

i)	the date specified in the Preamble as the date for commencement of the Works or the date when the Contractor receives:

ii)	such payment in advance of the commencement of the Works as may be specified in the terms of payment, or

iii)	notice of the issue of any import license necessary for commencing performance of the Contract, or

iv)	notice that any legal requirements necessary for the Contract to enter into force have been fulfilled, or

v)	notice that any necessary financial or administrative requirements specified in Part II as conditions precedent to commencement have been fulfilled.

1.1.2	"Conditions" means the Preamble to and these Conditions of Contract, Parts I and II.

1.1.3	"Contract" means the agreement between the Employer and the Contractor for the execution of the Works incorporating the Conditions, Specification, Employer's Drawings and Contractor's Drawings, priced and completed Schedules, Tender, Letter of Acceptance and such further documents as may be expressly incorporated by the Letter of Acceptance.

1.1.4 	"Contract Agreement" means the documents recording the terms of the Contract between the Employer and the Contractor.

1.1.5	"Contract Price" means the sum stated in the Letter of Acceptance as payable to the Contractor for the execution of the Works.

1.1.6	"Contractor" means the person whose tender has been accepted by the Employer and the legal successors in title to the Contractor but not (except with the consent of the Employer) any assignee of the Contractor.

1.1.7	"Contractor's Drawings' means all drawings, samples, patterns, models and operation and maintenance manuals to be submitted by the Contractor in accordance with Clause 6.

1.1.8	"Contractor's Equipment" means all appliances or things of whatsoever nature required for the purposes of the Works but does not include Plant.

1.1.9	"Contractor's Risks" means the risks defined in Sub-Clause 37.3.

1.1.10	"Defects Liability Certificate" means the certificate to be issued by the Engineer to the Contractor in accordance with Sub-Clause 30.11.

1.1.11	"Defects Liability Period" means one year or the period stated in Part II following taking over, during which the Contractor is responsible for making good defects and damage in accordance with Clause 30.

1.1.12	“Employer" means the person named as such in the Preamble and the legal successors in title to the Employer but not (except with the consent of the Contractor) any assignee of the Employer.

1.1.13 	"Employer's Drawings" means all the drawings and information provided by the Employer or the Engineer to the Contractor under the Contract.

1.1.14	"Employer's Risks” means those risks defined in Sub-Clause 37.2.

1.1.15	"Engineer” means the person appointed by the Employer to act as Engineer for the purposes of the Contract and designated as such in the Preamble

1.1.16	"Engineer's Representative" means any representative of the Engineer appointed from time to time by the Engineer under Sub-Clause 2.2.

1.1.17	"Final Certificate of Payment", means the certificate to be issued by the Engineer to the Employer in accordance with Sub-Clause 33.10.

1.1.18	"Force Majeure" has the meaning assigned to it under Sub-Clause 44.1.

1.1.19	"Foreign Currency" means a currency of a country other than that in which Plant is to be installed.

1.1.20	"Gross Misconduct" means any act or omission of the Contractor in violation of the most elementary rules of diligence which a conscientious contractor in the same position and under the same circumstances would have followed.

1.1.21	"Letter of Acceptance" means the formal acceptance by the Employer of the Tender incorporating any adjustments or variations to the Tender agreed between the Employer and the Contractor.

1.1.22	"Performance Security" means the security to be provided by the Contractor in accordance with Sub-clause 10.1. for the due performance of the Contract.

1.1.23	"Plant” means machinery, apparatus, materials and all things to be provided under the Contract for incorporation in the Works.

1.1.24	"Programme" means the Programme to be submitted by the Contractor in accordance with Sub-Clause 12.1 and any approved revision thereto.

1.1.25	"Provisional Sum" means a sum, described as such for the execution of work or for the supply of goods or services, to be used in accordance with Sub-Clause 36.1.

1.1.26	"Risks Transfer Date" means the date when the risk of loss of or damage to the Works passes from the Contractor to the Employer in accordance with Sub-Clause 39.1.

1.1.27	"Schedule of Prices" means the completed and priced Schedule of Prices, or any part or individual schedule thereof, submitted by the Contractor with his Tender and forming a part of the Contract documents.

1.1.28	"Section" means a part of the Works specifically identified as such as in the Contract.

1.1.29	"Site" means the place or places, provided or made available by the Employer where work is to be done by the Contractor or to which Plant is to be delivered, together with so much of the area surrounding the same as the Contractor shall with the consent of the Employer use in connection with the Works otherwise than merely for the purposes of access.

1.1.30	"Specification" means the specification of the Works included in the Contract and any modification thereof made in accordance with Clause 31.

1.1.31	"Subcontractor" means any person (other than the Contractor) named in the Contract for any part of the Works, or any person to whom any part of the Contract has been subcontracted with the consent of the Engineer, and the Subcontractor's legal successors in title but not any assignee of the Subcontractor.

1.1.32	"Taking-Over Certificate" means the certificate to be given by the Engineer to the Contractor in accordance with Clause 29.

1.1.33	"Tender" means the Contractor's priced offer to the Employer for the Execution of the Works.

1.1.34	"Tests on Completion" means the tests specified in the Contract or otherwise agreed by the Engineer and the Contractor to be performed before the Works are taken over by the Employer.

1.1.35	"Time for Completion" means the time stated in the Preamble for completing the Works or any Section thereof and passing the Tests on Completion calculated from the Commencement Date unless extended in accordance with Clause 26.

1.1.36	"Variation Order" means any written order, identified as such, issued to the Contractor by the Engineer under Sub-Clause 31.1.

1.1.37	"Works" means all Plant to be provided and work to be done by the Contractor under the Contract.

1.2	Headings and Titles

The headings and titles in these Conditions shall not be deemed part thereof or be taken into consideration in the interpretation or construction of the Contract.

1.3	Interpretation

Words importing persons or parties shall include firms and corporations and any organisation having legal capacity.

Words importing the singular only also include the plural and vice versa where the context requires.

1.4	Written Communications

Wherever in the contract provision is made for a communication to be "written" or "in writing” this means any hand-written, type-written or printed communication, including telex, cable and facsimile transmission.

1.5	Notices, Consents and Approvals

Wherever in the Contract provision is made for the giving of notice, consent or approval by any person, such consent or approval shall not be unreasonably withheld. Unless otherwise specified, such notice, consent or approval shall be in writing and the word "notify" shall be construed accordingly.

1.6	Costs, Overhead Charges and Profit

Whenever by these Conditions the Contractor is entitled to be paid cost, such cost shall be properly incurred and shall include any overhead charges properly allocable thereto but not profit unless so stated. Any profit entitlement shall be added to cost at the percentage stated in the Preamble.

1.7	Periods

In these Conditions "days" means calendar day and "year" means 365 days.

Engineer and Engineer's Representative

2.1	Engineer's Duties

The Engineer shall carry out the duties specified in the Contract.

If the Engineer is required, under the terms of his appointment by the Employer, to obtain the specific approval of the Employer before carrying out any of these duties, full particulars of such requirements shall be set out in Part II.

Except as expressly stated in the Contract the Engineer shall have no authority to relieve the Contractor of any of his obligations under the Contract.

2.2	Engineer's Representative

The Engineer's Representative shall be appointed by and be responsible to the Engineer and shall only carry out such duties and exercise such authority as may be delegated to him by the Engineer under Sub-Clause 2.3.

2.3	Engineer's Power to Delegate

The Engineer may from time to time delegate to the Engineer's Representative any of the duties vested in the Engineer and may at any time revoke such delegation.

Any such delegation or revocation shall be in writing and shall not take effect until a copy thereof has been delivered to the Contractor and the Employer.

Any decision, instruction or approval given by the Engineer's Representative to the Contractor in accordance with such delegation shall have the same effect as though it had been given by the Engineer. However:

(a) any failure of the Engineer's Representative to disapprove any Plant or workmanship shall not prejudice the right of the Engineer to disapprove such Plant or workmanship and to give instructions for the rectification thereof;

(b) if the Contractor questions any decision or instruction of the Engineer's Representative he may refer the matter to the Engineer who shall confirm, reverse or vary such decision or instruction.

2.4	Engineer to Act Impartially

Wherever under the Contract the Engineer is required to exercise his discretion by:

(a) giving his decision, opinion or consent. or

(b) expressing his satisfaction or approval, or

(c) determining value, or

(d) otherwise taking action which may affect the rights and obligations of the Employer or the Contractor,

he shall exercise such discretion impartially within the terms of the Contract and having regard to all the circumstances.

2.5	Engineer's Decisions and Instructions

The Contractor shall proceed with the decisions and instructions given by the Engineer in accordance with these Conditions.

2.6	Confirmation in Writing

The Contractor may require the Engineer to confirm in writing any decision or instruction of the Engineer which is not in writing. The Contractor shall notify the Engineer of such requirement without undue delay. Such a decision or instruction shall not be effective until written confirmation thereof has been received by the Contractor.

2.7 	Disputing Engineer's Decisions and Instructions

If the Contractor disputes or questions any decision or instruction under Clause 2.5 or a written confirmation under Clause 2.6, he shall give notice to the Engineer within 28 days after receipt thereof, giving his reasons.

The Engineer shall within a further period of 28 days by notice to the Contractor and the Employer with reasons, confirm, reverse or vary such decision or instruction.

If either party disagrees with the action taken by the Engineer, or if the Engineer fails to reply to the Contractor's notice within the stipulated 28 days, and the matter cannot be settled amicably that party shall be at liberty, subject to Sub-Clause 50.1, to refer the matter to arbitration in accordance with the Contract.

2.8	Replacement of Engineer

The Employer shall not appoint any person to act in replacement of the Engineer without the consent of the Contractor.

Assignment and Subcontracting

3.1	Assignment

The Contractor shall not assign the Contract or any part of his obligations under the Contract. A charge in favour of the Contractor's bankers of any monies due under the Contract shall not be considered an assignment.

4.1	Subcontracting

The Contractor shall not subcontract the whole of the Works.

Except where otherwise provided by the Contract the Contractor shall not subcontract any part of the Works without the prior consent of the Engineer.

The Contractor shall however, not require such consent for purchases of materials or to place contracts for minor details or for any part of the Works of which the manufacturer or supplier is named in the Contract.

The Contractor shall be responsible for the acts, defaults and neglects of any Subcontractor, his agents or employees as fully as if they were the acts, defaults or neglects of the Contractor, his agents or employees.

Contract Documents

5.1		Ruling Language

Where versions of the Contract are prepared in different languages, the version which is to prevail shall be specified in the Preamble. The language of such version is referred to as the ruling language.

5.2	Day to Day Communications

The language for day to day communications is stated in the Preamble.

5.3	Priority of Contract Documents

Unless otherwise provided in the Contract the priority of the Contract documents shall as follows:

1.	The Letter of Acceptance

2.	The Preamble

3.	The Conditions of Contract, Part II

4.	The Conditions of Contract, Part I

5.	Any other documents forming part of the Contract.

5.4	Documents Mutually Explanatory

Subject to Sub-Clause 5.3. the Contract documents shall be taken as mutually explanatory. any ambiguities or discrepancies shall be resolved by the Engineer, who shall then instruct the Contractor thereon.

If the Contractor considers that compliance with such instructions will result in any cost which the Contractor could not reasonably have anticipated, he shall forthwith inform the Engineer with full supporting details. The Engineer shall then, if he approves, certify such costs as may be reasonable, together with profit where appropriate, which shall be added to the Contract Price.

If on the other hand compliance with such instructions results in the most advantageous evaluated Bid costs for the Contractor then he had reason to anticipate, the Engineer shall certify a deduction from the Contract Price allowing for profit where appropriate.

6.1	Contractor's Drawings

The Contractor shall submit to the Engineer for approval:

(a) within the time given in the Contract or in the Programme such drawings, samples, models or information as may be called for therein, and in the numbers therein required, and

(b) during the progress of the Works, such drawings of the general arrangement and details of the Works as specified in the Contract or as the Engineer may require.

The Engineer shall signify his approval or disapproval thereof. If he fails to do so within the time given in the Contract or the Programme or if no time limit is specified, within 28 days of receipt, they shall be deemed to be approved.

Approved drawings, samples and models shall be signed or otherwise identified by the Engineer.

The Contractor shall supply additional copies of approved drawings in the form and numbers stated in the Contract.

6.2	Consequences of Disapproval of Contractor's Drawings

Any Contractor's Drawings which the Engineer disapprove shall be forthwith modified to meet the requirements of the Engineer and shall be re-submitted.

6.3	Approved Contractor's Drawings

Approved Contractor's Drawings shall not be departed from except as provided in Clause 31.

6.4	Inspection of Contractor's Drawings

The Engineer shall have the right at all reasonable times to inspect, at Contractor's premises, all Contractor's Drawings of any part of the Works.

6.5	Erection Information

The Contractor shall provide, within the times stated in the Contract or in the Programme, drawings showing how the Plant is to be affixed and any other information required for:

(a)	preparing suitable foundations or other means of support, and

(b)	providing suitable access on the Site for the Plant and any necessary equipment to the place where the Plant is to be erected, and

(c)	making necessary connections to the Plant

6.6	Operation and Maintenance Manuals

Before the Works are taken over in accordance with Clause 29 the Contractor shall supply operation and maintenance manuals together with drawings of the Works as built. These shall be in such detail as will enable the Employer to operate, maintain, adjust and repair all parts of the Works.

Unless otherwise stated in Part II the manuals and drawings shall be in the ruling language, and in such form and numbers as stated in the Contract.

Unless otherwise agreed, the Works shall not be considered to be completed for the purposes of taking over until such manuals and drawings have been supplied to the Employer.

6.7	Employer's Use of Contractor's Drawings

Contractor's Drawings may be used by the Employer for no other purpose than completing, operating, maintaining, adjusting and repairing the Works.

6.8	Contractor's Use of Employer's Drawings

The Employer's Drawings, Specification and other information submitted by the Employer or the Engineer to the Contractor shall remain the property of the Employer. They shall not, without the consent of the Employer, be used, copied or communicated to a third party by the Contractor unless necessary for the purposes of the Contract.

6.9	Manufacturing Drawings

Unless otherwise specified in Part II the Contractor shall not be required to disclose to the Employer or the Engineer the Contractor's confidential manufacturing drawings, designs, know-how or manufacturing practices, processes or operations.

7.1	Errors in Contractor's Drawings

The Contractor shall be responsible for any errors or omissions in the Contractor's Drawings unless they are due to incorrect Employer's Drawings or other written information supplied by the Employer or the Engineer. Approval by the Engineer of the Contractor's Drawings shall not relieve the Contractor from any responsibility under this Sub-Clause.

The Contractor shall bear any costs he may incur as a result of delay in providing Contractor's Drawings and other information or as a result of errors or omissions therein, for which the Contractor is responsible.

The Contractor shall at his own cost carry out any alterations or remedial work necessitated by such errors or omissions for which he is responsible and modify the Contractor's Drawings and such other information accordingly.

The performance of his obligations under this Clause shall be in full satisfaction of the Contractor's liability under this Clause but shall not relieve him of his liability under Sub-Clause 27.1.

7.2	Errors by Employer or Engineer

The Employer shall be responsible for the Employer's Drawings and for other written information supplied by the Employer or the Engineer and for the details of special work specified by either of them. If such Employer's Drawings, information or details are incorrect and necessitate alterations of the work, the Employer shall pay the Contractor the cost of the alterations together with profit as certified by the Engineer.

Obligations of the Contractor

8.1	General Obligations

The Contractor shall, in accordance with the Contract, with due care and diligence, design, manufacture, deliver to Site, erect, test and commission the Plant and carry out the Works within the Time for Completion. The Contractor shall also provide all necessary Contractor's Equipment, superintendence, labor and, except as stated in Part II, all necessary facilities there for.

8.2	Setting Out

The Contractor shall set out the Works in relation to original points, lines and levels of reference given by the Engineer in writing and provide all necessary instruments, appliances and labor for such purposes.

If, at any time during the execution of the Works, any error appears in the positions, levels, dimensions or alignment of the Works, the Contractor shall rectify the error.

The Contractor shall bear the cost of rectifying the error, unless the error results from incorrect information supplied in writing by the Employer, the Engineer or from default by another contractor, in which case the cost together with profit shall be borne by the Employer.

The checking of any setting-out by the Engineer shall not relieve the Contractor of his responsibility for the accuracy thereof.

9.1	Contract Agreement

The Contractor shall, if called upon so to do, execute a Contract Agreement recording all the terms of the Contract, to be prepared by and completed at the cost of the Employer in the form annexed hereto.

10.1	Performance Security

If Part II requires the Contractor to obtain a Performance Security, he shall obtain the same in the sum required, within 28 days after the receipt of the Letter of Acceptance. The Performance Security shall be provided by a person and in a form approved by the Employer. The cost of complying with the requirements of this Clause shall be borne by the Contractor.

10.2	Period of Validity

The Performance Security shall be valid until the Contractor has executed, completed and remedied defects in the Works in accordance with the Contract. No claim shall be made against the Performance Security after the issue of the Defects Liability Certificate and the Performance Security shall be returned to the Contractor within 14 days of the issue of the Defects Liability Certificate.

10.3	Claims under Performance Security

Whether or not the Performance Security is stated by its terms to be payable on the demand of the Employer the Employer shall not make a claim under the Performance Security unless one of the following conditions is satisfied:

(a)	the Contractor is in breach of the Contract and fails to remedy the breach within 42 days after receiving written notice from the Employer requiring him so to do. The notice shall state the intention to claim under the Performance Security, the amount claimed and the breach relied upon, or

(b)	the Employer and the Contractor have agreed in writing that the amount demanded is payable to the Employer, and the amount has not been paid within 42 days thereafter, or

(c)	the Employer has obtained an award in arbitration under Clause 50 and the amount awarded has not been paid within 42 days after the award, or

(d)	the Contractor has gone into liquidation or is bankrupt.

In every case the Employer shall, when making the claim, send a copy to the Contractor.

11.1	Site Data

The Tender shall be deemed to have been based on such data on climatic, hydrological and general conditions on the Site and for the operation of the Works as the Employer or the Engineer has made available to the Contractor for the purposes of the Tender. The Contractor shall be responsible for his own interpretation of such data.

11.2	Sufficiency of Contract Price

The Contractor shall be deemed to have satisfied himself on and taken account of in his Tender:

(a)	all the conditions and circumstances affecting the Contract Price,

(b)	the possibility of carrying out the Works as described in the Contract,

(c)	the general circumstances at the Site (if access has been made available to him) and

(d)	the general Labour position at the Site.

The Contractor shall not be responsible for the accuracy of information given in writing by the Employer or the Engineer but shall be responsible for his interpretation of information received from whatever source.

11.3	Physical Obstructions and Conditions

If during the execution of the Works on Site the Contractor encounters physical obstructions or conditions of the kind stipulated in Sub-Clause 26.1.c) the Contractor shall be entitled to recover the additional cost incurred in consequence.

The Engineer shall certify and there shall be added to the Contract Price the additional cost of:

(a)complying with any instruction which the Engineer, after due consultation with the Employer and the Contractor, issues to the Contractor in connection therewith, and

(b)any necessary measures which the Contractor may take in the absence of specific instructions from the Engineer.

12.1	Programme to be Furnished

The Contractor shall submit to the Engineer for his approval the Programme which shall contain the following:

(a)the order in which the Contractor proposes to carry out the Works (including design, manufacture, delivery to Site, erection, testing and commissioning),

(b)the times when submission and approval of the Contractor's Drawing are required,

(c)	the times by which the Contractor requires the Employer:

(i)	to furnish any Employer's Drawings,

(ii)	to provide access to the Site,

(iii)	to have completed the necessary civil engineering work (including foundations for the Plant) and

(iv)	to have obtained any import licenses, consents, wayleaves and approvals necessary for the purpose of the Works.

The Contractor shall submit the Programme in the form stated in the Preamble within 28 days after the Commencement Date.

The approval by the Engineer of the Programme shall not relieve the Contractor or the Employer from any obligation under the Contract.

12.2	Alteration to Programme

No material alteration to the Programme shall be made without the approval of the Engineer.

12.3	Revision of Programme

If the progress of the Works does not conform to the Programme, the Engineer may instruct the Contractor to revise the Programme.

If such modifications are required for reasons for which the Contractor is not responsible, the cost of preparing the revised Programme shall be certified by the Engineer and added to the Contract Price.

13.1	Contractor's Representative

The Contractor shall employ one or more competent representatives to superintend the carrying out of the Works on Site. They shall be fluent in the language for day to day communications. Their names shall be communicated in writing to the Engineer before work on Site begins.

Any instruction or notice which the Engineer gives to the Contractor's representative shall be deemed to have been given to the Contractor.

13.2	Objection to Contractor's Employees

The Contractor shall, upon the Engineer's written instruction, remove from the Works any person employed by him in the execution of the Works, who misconducts himself or is incompetent or negligent.

14.1	Contractor's Equipment

Except to the extent specified in Part II, the Contractor shall provide all Contractor's Equipment necessary to complete the Works.

All Contractor's Equipment shall, when brought on to the Site, be deemed to be exclusively intended for the execution of the Works. The Contractor shall not remove from the Site any such equipment, except:

(a) when it is no longer required for the completion of the Works, or

(b)when the Engineer has given his consent.

14.2	Safety Precautions

The Contractor shall observe all applicable regulations regarding safety on the Site.

Unless otherwise agreed, the Contractor shall, from the commencement of work on Site until taking over provide:

(a)fencing, lighting, guarding and watching of the Works, and

(b)temporary roadways, footways, guards and fences which may be necessary for the accommodation and protection of owners and occupiers of adjacent property, the public and others.

14.3	Electricity Water and Gas

The Contractor shall be entitled to use for the purposes of the Works such supplies of electricity, water, gas and other services as may be available on the Site and of which details are given in the Preamble. The Contractor shall pay the Employer a fair price for such use. The Contractor shall at his own cost provide any apparatus necessary for such use.

14.4	Employer's Equipment

The Employer shall, if the Contractor so requests for the execution of the Works, operate any available equipment of which details are given in the Preamble. The Contractor shall pay the Employer a fair price for such use.

The Employer shall during such operation retain control of and be responsible for the safe working of the equipment.

14.5	Clearance of Site

The Contractor shall from time to time during the progress of the Works clear away and remove all surplus materials and rubbish. On completion of the Works the Contractor shall remove all Contractor's Equipment and leave the whole of the Site and the Works clean and in a workmanlike condition, to the satisfaction of the Engineer.

14.6	Opportunities for Other Contractors

The Contractor shall, in accordance with the Engineer's instructions, afford to other contractors engaged by the Employer to work on the Site and persons lawfully upon the Site all reasonable opportunities for carrying out their work provided that the same shall not obstruct or disturb the progress of the Works. The Contractor shall also afford such opportunities to the employees of the Employer.

If the Contractor, on the written request of the Engineer, makes available any Contractor's Equipment or provides any other service, the Employer shall pay the Contractor accordingly. The amount to be paid shall be certified by the Engineer and added to the Contract Price.

14.7	Authority for Access

No persons other than the employees of the Contractor and his Subcontractors shall be allowed on the Site except with the consent of the Engineer.

Facilities to inspect the Works shall at all times be afforded by the Contractor to the Engineer and his representative, the Employer's representatives, authorities and officials.

14.8	Information for Import Permits and Licenses

The Contractor shall submit to the Employer in good time such details of all Plant and Contractor's Equipment as will enable the Employer to obtain all necessary import permits or licenses.

15.1	Compliance with Statutes, Regulations

The Contractor shall, in all matters arising in the performance of the Contract, comply in all respects with, give all notices and pay all fees required by the provisions of any national or state statute, ordinance or other law or any regulation or bye-law of any duly constituted authority.

15.2	Compliance with Laws

The Contractor shall comply with the laws of the country of manufacture concerning the manufacture of the Plant, and the laws of the country where the Plant is to be erected so far as such laws concern the manufacture, erection and operation of the Works.

16.1	Patent Rights

The Contractor shall indemnify the Employer against all claims of infringement of any patent, registered design, copyright, trade mark or trade name or other intellectual property right provided that all of following conditions are satisfied:

(a)The claim or proceedings arise out of the design, construction, manufacture or use of Works or any Plant supplied by the Contractor.

(b)The right was protected at the date of the Contract in the Contractor's country or the country in which the Plant is to be manufactured or erected.

(c)The infringement or allegation of infringement was not caused by any use of the Works otherwise than for purpose indicated by or reasonably to be inferred from date Specification.

(d)The infringement or allegation of infringement was not caused by the use of any Plant in association or combination with any plant not supplied by the Contractor, unless such association or combination was disclosed to the Contractor prior to the due of the Tender.

(e)The infringement of or allegation of infringement was not caused by the Contractor following the design or instructions of the Employer or the Engineer.

16.2	Claims in respect of Patent Right

The Contractor shall be promptly notified of any claim under this Clause made against the Employer. The Contractor may at his own cost conduct negotiations for the settlement of such claim, and any litigation that may arise therefrom.

The Employer shall not make any admission which might be prejudicial to the Contractor unless the Contractor has failed to take over the conduct of the negotiations or litigation within a reasonable time after having been so requested.

The Contractor may not, however, conduct such negotiations or litigation before he has given the Employer such reasonable security as the Employer may require. The security shall be for an amount which is an assessment of the compensation, damages, expenses and costs for which the Employer may become liable and which are the subject of the indemnity under Sub-Clause 16.1

The Employer shall, at the request of the Contractor, provide all available assistance for the purpose of contesting any such claim or action, and shall be repaid all reasonable costs incurred in so doing.

16.3	Employer's Warranty for Patent Rights

If any matter for which the Contractor is not liable to indemnify the Employer under Sub-Clause 16.1 causes the infringement or allegation of infringement by the Contractor of any patent, registered design, trade mark, copyright or other intellectual property right, the Employer shall indemnify the Contractor against all claims damages, expenses and costs which the Contractor may incur in relation thereto. The provisions of Sub-Clause 16.2 shall apply mutatis mutandis.

Obligations of the Employer

17.1	Access to and Possession of the Site

The Employer shall in reasonable time grant the Contractor access to and possession of the Site, which may, however, not be exclusive to the Contractor.

The Employer shall to the extent stated in the Specification provide means of access for the delivery of all Plant and Contractor's Equipment to the Site.

17.2	Assistance with Local Regulations

The Employer shall assist the Contractor in ascertaining the nature and extent of any laws, regulations, orders or bye-laws, and customs in the country where the Plant is to be erected, which may affect the Contractor in the performance of his obligations under the Contract. The Employer shall if so requested procure for the Contractor copies thereof and information relating thereto at the Contractor's cost.

17.3	Civil Works on Site

Any building, structure, foundation or means of access on the Site to be provided by the Employer shall be in a condition suitable for the reception, movement, installation and maintenance of the Works within the time or times indicated in the Programme.

17.4	Consents and Wayleaves

The Employer shall in due time obtain or grant all consents including permits-to-work, wayleaves and approvals required for the Works.

17.5	Import Permits and Licenses

The Employer shall obtain all import permits or licenses required for any part of the Plant or Works in reasonable time having regard to the time for delivery of the Plant and completion of the Works.

18.1	Engagement of Labour

The Contractor shall, unless otherwise provided in the Contract, make his own arrangements for the engagement of all labour and for their payment, housing feeding and transport.

18.2	Returns of Labour

The Contractor shall submit detailed returns showing the supervisory staff and the numbers of the several classes of labour from time to time employed by the Contractor and Subcontractors on the Site. The returns shall be submitted in such form and at such intervals as the Engineer may prescribe.

18.3	Working Hours

On the Site the Contractor shall observe the normal working hours stated in the Preamble. The Employer shall allow the Contractor to carry out work on the Site continuously during such working hours.

The Engineer may after consulting the Employer and the Contractor, direct that work shall be done at other times. The extra cost, together with profit, shall be added to the Contract Price unless it has become necessary for the completion of the Works within the Time for Completion, and this is due to the default of the Contractor.

18.4	Restriction on Working Hours

No work shall be carried out on the Site outside normal working hours or on the locally recognised days of rest, unless:

(a)	the Contract so provides, or

(b)	the work is unavoidable or necessary for the saving of life or property or for the safety of the Works, in which case the Contractor shall immediately advise the Engineer, or

(c)	the Engineer gives his consent.

Workmanship and Materials

19.1	Manner of Execution

All Plant to be supplied shall be manufactured and all work to be done shall be executed in the manner set out in the Contract.

Where the manner of manufacture and execution is not set out in the Contract, the work shall be executed in a proper and workmanlike manner in accordance with recognized good practice.

19.2	Covering up Work

The Contractor shall give the Engineer full opportunity to examine, measure and test any work on Site which is about to be covered up or put out of view.

The Contractor shall give due notice to the Engineer whenever such work is ready for examination, measurement or testing.

The Engineer shall then, unless he notifies the Contractor that he considers it unnecessary, without unreasonable delay carry out the examination, measurement or testing.

19.3	Uncovering Work

If so instructed by the Engineer, the Contractor shall expose any parts of the Works. The Contractor shall reinstate and make good such parts to the Engineer's satisfaction.

If any parts of the Works have been covered up or put out of view by the Contractor after complying with Sub-Clause 19.2 and are found to be in accordance with the Contract the cost incurred by the Contractor in complying with the Engineer's instructions including profit shall be certified by the Engineer and added to the Contract Price.

20.1	Independent Inspection

The Engineer may, if so provided in the Contract or with the Contractor's consent, delegate inspection and testing of Plant to an independent inspector. Any such delegation shall be effected in the manner required by Sub-Clause 2.3, and for this purpose such independent inspector shall be considered as an Engineer's Representative. Notice of such appointment (being not less than 14 days) shall be given by the Engineer to the Contractor.

20.2 	Inspection and Testing During Manufacture

The Engineer shall be entitled during manufacture to inspect, examine and test the materials and workmanship and check the progress of manufacture of all Plant to be supplied under the Contract. This shall take place on the Contractor's premises during working hours. If Plant is being manufactured on other premises, the Contractor shall obtain permission for the Engineer to carry out such inspection, examination and testing on those premises.

No such inspection, examination or testing shall release the Contractor from any obligation under the Contract.

20.3	Dates for Inspection and Testing

The Contractor shall agree with the Engineer the time and place for the testing of any Plant as provided in the Contract. The Engineer shall give the Contractor 24 hours’ notice of his intention to attend the tests.

If the Engineer does not attend on the date agreed, the Contractor may, unless the Engineer instructs the Contractor not to do so, proceed with the tests, which shall be deemed to have been made in the Engineer's presence.

The Contractor shall forthwith forward to the Engineer duly certified copies of the test results. If the Engineer has not attended the test, he shall accept the validity of the test readings.

20.4	Facilities for Testing

Where the Contract provides for tests on the premises of the Contractor or of any Sub-contractor, the Contractor shall provide such assistance, labour materials, electricity, fuel, stores, apparatus and instruments as may be necessary to carry out the test efficiently.

20.5	Certificate of Testing

When Plant has passed the tests referred to in this Clause, the Engineer shall furnish to the Contractor a certificate or endorse the Contractor's test certificate to that effect.

21.1	Rejection

If, as a result of the inspection, examination or testing referred to in Clause 20, the Engineer decides that any Plant is defective or otherwise not in accordance with the Contract, he may reject such Plant and shall notify the Contractor thereof immediately. The notice shall state the Engineer's objections with reasons. The Engineer shall not reject any Plant for minor defects which do not affect the commercial operation of such Plant.

The Contractor shall then with all speed make good the defect or ensure that any rejected Plant complies with the Contract.

If the Engineer requires such Plant to be retested, the tests shall be repeated under the same terms and conditions. All costs incurred by the Employer by the repetition of the tests shall be deducted from the Contract Price.

22.1	Permission to Deliver

The Contractor shall apply in writing to the Engineer for permission to deliver any Plant or Contractor's equipment to the Site. No Plant or Contractor's Equipment may be delivered to the Site without the Engineer's written permission.

The Contractor shall be responsible for the reception on Site of the Plant and Contractor's Equipment.

Suspension of Works, Delivery or Erection

23.1	Order to Suspend

The Engineer may at any time instruct the Contractor to:

(a)suspend progress of the Works, or

(b)suspend delivery of Plant or Contractor's Equipment which is ready for delivery to the Site at the time for delivery specified in the Programme, or if no time is specified, at the time appropriate for it to be delivered, or

(c)suspend the erection of Plant which has been delivered to the Site,

When the Contractor is prevented from delivering or erecting Plant in accordance with the Programme the Engineer shall be deemed to have instructed a suspension except when such prevention is caused by the Contractor's default.

The Contractor shall during suspension protect and secure the Works or Plant affected at the Contractor's works or elsewhere or at the Site, as the case may be, against any deterioration, loss or damage.

24.1	Cost of Suspension

The additional cost incurred by the Contractor in protection, securing and insuring the Works or Plant and in following the Engineer's instructions under Sub-Clause 23.1 and in resumption of the work, shall be added to the Contract Price.

The Contractor shall not be entitled to be paid any additional costs if such suspension is necessary by reason of a default on the part of the Contractor.

The Contractor shall not be entitled to additional costs unless he notifies the Engineer of his intention to make such claim, within 28 days after receipt of the order to suspend progress or delivery or of the date of deemed suspension under Sub-Clause 23.1.

24.2	Payment in Event of Suspension

The Contractor shall be entitled to payment for Plant which has not been delivered to Site if the work on Plant or delivery of Plant has been suspended for more than 28 days. After 28 days of suspension, the Contractor shall be entitled to payment of the value of such Plant as at the date of suspension.

A certificate of payment shall be issued on condition that:

(a)the Contractor has marked the Plant as the Employer's property in accordance with the Engineer's instructions, and

(b)the suspension is not due to the Contractor's default.

24.3	Prolonged Suspension

If suspension under Clause 23.1. has continued for more than 84 days, and the suspension is not due to the Contractor's default, the Contractor may by notice to the Engineer require permission to proceed within 28 days.

If permission is not granted within that time, the Contractor may treat the suspension as an omission under Clause 31 of the Section it affects, or if the suspension affects the whole of the Works, terminate the Contract and the provisions of Clause 46 shall apply.

24.4	Resumption of Work

If the Contractor chooses not to treat prolonged suspension as an omission or termination under Sub-Clause 24.3, the Employer shall upon the request of the Contractor, take over the responsibility for protection, storage, security and insurance of the suspended Works and the risk of loss or damage thereto shall thereupon pass to the Employer.

After receipt of permission or an order to proceed, the Contractor, shall after due notice to the Engineer, examine the Works and the Plant affected by the suspension. The Contractor shall make good any deterioration or defect in or loss of the Works or Plant that may have occurred during the suspension. Cost properly incurred by the Contractor which would not have been incurred but for the suspension shall be added to the Contract Price together with profit.

The Contractor shall not be entitled to payment for costs incurred in making good any deterioration, defect or loss caused by faulty workmanship or materials or by the Contractor's failure to take the measures specified in Sub-Clause 23.1.

If the Employer has taken over risk and responsibility for the suspended Works under this Sub-Clause, risk and responsibility shall revert to the Contractor 14 days after receipt of the permission or order to proceed.

Completion

25.1	Time for Completion

The Works shall be completed and shall have passed the Tests on Completion within the Time for Completion

26.1	Extension of Time for Completion

The Contractor may claim an extension of the Time for Completion if he is or will be delayed in completing the Works by any of the following causes:

(a)extra or additional work ordered in writing under Clause 31,

(b)exceptional adverse weather conditions,

(c)physical obstructions or conditions which could not reasonably have been foreseen by the Contractor,

(d)Employer's or Engineer's instructions, otherwise than by reason of the Contractor's default,

(e)the failure of the Employer to fulfil any of his obligations under the Contract,

(f)delay by any other contractor engaged by the Employer,

(g)any suspension of the Works under Clause 23, except when due to the Contractor's default,

(h)any industrial dispute,

(i)the Employer's Risks,

(j)Force Majeure.

The Contractor shall give to the Engineer notice of his intention to make a claim for an extension of time within 14 days of the circumstances for such a claim becoming known to the Contractor. The notice shall be followed as soon as possible by the claim with full supporting details.

The Engineer shall, after due consultation with the Employer and the Contractor, grant the Contractor from time to time, either prospectively or retrospectively, such extension of Time for Completions as may be justified. The Engineer shall notify the Employer and the Contractor accordingly.

The Contractor shall be entitled to such extension whether the delay occurs before or after the Time for Completion.

26.2	Delays by Subcontractors

The Contractor shall be entitled to claim an extension of time if delay on the part of a Subcontractor is due to a cause mentioned in Clause 26.1, and such delay prevents the Contractor from meeting the Time for Completion.

26.3	Earlier Completion

The Employer may require completion of the Works or part thereof earlier than the Time for Completion, on the following conditions:

(a)The Employer and the Contractor shall first agree the extra sum to be paid for each day by which the Contractor completes the Works or part thereof earlier than the Time for Completion.

(b)The Contractor shall not become liable under Sub-Clause 27.1 for any failure to complete the Works or the part thereof by the earlier time.

27.1	Delay in Completion

If the Contractor fails to complete the Works within the Time for Completion, the Employer shall be entitled to a reduction in the Contract Price unless it can be reasonably concluded from circumstance that the Employer will suffer no loss.

The Employer shall within a reasonable time give the Contractor notice of his intention to claim a reduction.

The reduction shall be the percentage per day stated in the Preamble of that part of the Contract Price which is attributable to such part of the Works as cannot in consequence of the failure be put to the intended use. The reduction shall be computed for each day between the Time for Completion and the actual date of completion.

The reduction shall in no case exceed the maximum percentage of the Contract Price of such part stated in the Preamble.

Except as provided in Sub-Clause 27.2, such reduction shall be to the exclusion of any other remedy of the Employer in respect of the Contractor's failure to complete within the Time for Completion.

27.2	Prolonged Delay

If the Employer has become entitled to the maximum reduction under Clause 27.1 for any part of the Works, he may by notice require the Contractor to complete. Such notice shall fix a final time for completion which shall be reasonable.

If the Contractor fails to complete within such time, and this is not due to a cause for which the Employer or some other contractor employed by him is responsible, the Employer may by further notice to the Contractor either:

(a)require the Contractor to complete, or

(b)may himself complete at the Contractor's cost provided that he does so in a reasonable manner, or

(c)terminate the Contract.

If the Employer terminates the Contract, he shall be entitled to recover from the Contractor any loss he has suffered up to the maximum amount stated in the Preamble. If no maximum amount is stated, the Employer shall not be entitled to recover more than that part of the Contract Price which is attributable to that part of the Works which cannot by reason of the Contractor's failure be put to the intended use.

The Employer shall give credit for the value of any part of the Works which he retains.

Tests on Completion

28.1	Notice of Tests

The Employer shall give to the Engineer 21 days’ notice of the date after which he will be ready to make the Tests on Completion (the Tests). Unless otherwise agreed, the Tests shall take place within 14 days after the said date on such day or days as the Engineer shall notify the Contractor.

28.2	Time for Tests

If the Engineer fails to appoint a time after having been asked to do so, or does not attend at the time and place appointed, the Contractor shall be entitled to proceed with the Test in his absence. The Tests shall then be deemed to have been made in the presence of the Engineer and the results of the Tests shall be accepted as accurate.

28.3	Delayed Tests

If the Tests are being unduly delayed by the Contractor the Engineer may by notice require the Contractor to make the Tests within 21 days after the receipt of such notice. The Contractor shall make the Tests on such days within that period as the Contractor may fix and of which he shall give notice to the Engineer.

If the Contractor fails to make the Tests within 21 days the Engineer may himself proceed with the Tests. All Tests so made by the Engineer shall be at the risk and cost of the Contractor and the cost thereof shall be deducted from the Contract Price. The tests shall then be deemed to have been made in the presence of the Contractor and the results of the Tests shall be accepted as accurate.

28.4	Facilities for Tests on Completion

Except where otherwise specified, the Employer shall provide free of charge such labour, materials, electricity, fuel, water, stores, apparatus and feedstock as may be reasonably required by the Contractor to carry out the Tests.

28.5	Retesting

If the Works or any Section fails to pass the Tests, the Engineer or the Contractor may require such Tests to be repeated on the same terms and conditions. All costs to which the Employer may be put by the repetition of the Tests under this Sub-Clause or under Sub-Clause 30.7 shall be deducted from the Contract Price.

28.6	Disagreement as to Result of Tests

If the Engineer and the Contractor disagree on the interpretation of the Test results, each shall give a statement of his views to the other within 14 days after such disagreement arises. The statement shall be accompanied by all relevant evidence.

28.7	Consequences of Failure to Pass Tests on Completion

If the Works or any Section fails to pass the Tests on the repetition thereof under Sub-Clause 28.5, the Engineer, after due consultation with the Employer and the Contractor, shall be entitled to:

(a)order one further repetition of the Tests under the conditions of Sub-Clause 28.5, or

(b)reject the Works or Section in which event the Employer shall have the same remedies against the Contractor as are provided under Sub-Clause 30.5 (c), or

(c)issue a Taking-Over Certificate, if the Employer so wishes, notwithstanding that the Works are not complete. The Contract Price shall then be reduced by such amount as may be agreed by the Employer and the Contractor or, failing agreement, as may be determined by arbitration.

28.8	Use by the Employer

In considering the results of Tests carried out under Sub-Clauses 29.3, 29.4 and 30.7 the Engineer shall make allowances for the effect of any use of the Works by the Employer on the Certificate to the performance or other characteristics of the Works.

28.9	Test Certificate

As soon as the Works or any Section thereof has passed the Tests, the Engineer shall issue a Certificate to the Contractor and the Employer to that effect.

Taking Over

29.1		Taking Over

The Works shall be taken over by the Employer when they have been completed in accordance with the Contract, except in minor respects that do not affect the use of the Works for their intended purpose, have passed the Tests on Completion and a Taking-Over Certificate has been issued or deemed to have been issued in accordance with Sub-Clause 29.2.

29.2	Taking-Over Certificate

The Contractor may apply by notice to the Engineer for a Taking-Over Certificate not earlier than 14 days before the Works will in the Contractor's opinion be complete and ready for taking over under Sub-Clause 29.1.

The Engineer shall within 28 days after the receipt of the Contractor's application either:

(a)issue the Taking-Over Certificate to the Contractor with a copy to the Employer stating the date on which the Works were complete and ready for taking over, or

(b)reject the application giving his reasons and specifying the work required to be done by the Contractor to enable the Taking-Over Certificate to be issued.

If the Engineer fails either to issue the Taking-Over Certificate or to reject the Contractor's application within the period of 28 days he shall be deemed to have issued the Taking-Over Certificate on the last day of that period.

If the Works are divided by the Contract into Sections the Contractor shall be entitled to apply for separate Taking-Over Certificate for each such Section

29.3	Use before Taking Over

The Employer shall not use any part of the Works unless a Taking-Over Certificate has been issued in respect thereof.

If nevertheless the Employer uses any part of the Works, that part which is used shall be deemed to have been taken over at the date of such use. The Engineer shall on request of the Contractor issue a Taking-Over Certificate accordingly. If the Employer uses any part of the Works before taking over the Contractor shall be given the earliest opportunity of taking such steps as may be necessary to carry out the Tests on Completion.

The provisions of Sub-Clause 27.1 shall not apply to any part of the Works while being so used by the Employer. Clause 30 shall apply as if the part had been taken over on the date it was taken into use.

29.4	Interference with Tests on Completion

If the Contractor is prevented from carrying out the Tests on Completion by a cause for which the Employer or the Engineer or other contractors employed by the Employer are responsible, the Employer shall be deemed to have taken over the Works on the date when the Tests on Completion would have been completed but for such prevention. The Engineer shall issue a Taking-Over Certificate accordingly.

The Works shall not be deemed to have been taken over if they are not substantially in accordance with the Contract.

If the Works are taken over under this Clause the Contractor shall nevertheless carry out the Tests on Completion during the Defects Liability Period. The Engineer shall require the Tests on Completion to be carried out by 14 days’ notice and in accordance with the relevant provisions of Clause 28.

Any additional costs to which the Contractor may be put in making the Tests on Completion during the Defects Liability Period, shall be added to the Contract Price.

Defects after Taking Over

30.1	Defects Liability Period

Where any part of the Works is taken over separately from the Works the Defects Liability Period for that part shall commence on the date it was taken over.

30.2	Making Good Defects

The Contractor shall, subject to Sub-Clause 30.9, be responsible of making good any defect in or damage to any part of the Works which may appear or occur during the Defects Liability Period and which arises from, either:

(a)any defective materials, workmanship or design, or

(b)any act or omission of the Contractor during the Defects Liability Period.

The Contractor shall make good the Defects or damage as soon as practicable and at his own cost.

30.3	Notice of Defects

If any such defect appears or damage occurs, the Employer or the Engineer shall forthwith notify the Contractor thereof.

30.4	Extension of Defects Liability Period

The provision of this Clause shall apply to all replacements or renewals carried out by the Contractor as if the replacements and renewals had been taken over on the date they were completed.

The Defects Liability Period for the Works shall be extended by a period equal to the period during which the Works cannot be used by reason of a defect or damage. If only part of the Works cannot be used by reason of a defect, the Defect Liability Period shall be extended only for that part.

In neither case shall the Defects Liability Period be extended by more than one year.

When erection or delivery of Plant has been suspended under Sub-Clause 23.1, the Contractor's obligations under this Clause shall not apply to any defects occurring more than three years after it would have been delivered but for the suspension or such period as may be stated in Part II.

30.5	Failure to Remedy Defects

If the Contractor fails to remedy a defect or damage within a reasonable time, the Employer may fix a final time for remedying the defect or damage.

If the Contractor fails to do so, the Employer may:

(a)carry out the work himself or by others at the Contractor's risk and cost, provided that he does so in a reasonable manner. The costs properly incurred by the Employer in remedying the defect or damage shall be deducted from the Contract Price, but the Contractor shall have no responsibility for such work, or

(b)require the Contractor to grant the Employer a reasonable reduction in the Contract Price to be agreed or fixed by arbitration under Clause 50, or

(c)if the defect or damage is such that the Employer has been deprived of substantially the whole of the benefit of the Works or a part thereof, he may terminate the Contract in respect of such parts of the Works as cannot be put to the intended use. The Employer shall to the exclusion of any remedy under Clause 45 be entitled to recover all sums paid in respect of such parts of the Works together with the cost of dismantling the same, clearing the Site and returning Plant to the Contractor or otherwise disposing of it in accordance with the Contractor's instructions.

30.6	Removal of Defective Work

If the defect of damage is such that repairs cannot be expeditiously carried out on the Site, the Contractor may with the consent of the Engineer or the Employer remove from the Site for the purposes of repair any part of the Works which is defective or damaged.

30.7	Further Tests on Completion

If the replacements or renewals are such that they may affect the performance of the Works the Employer may request that Tests on Completion be repeated to the extent necessary. The request shall be made by notice within 28 days after the replacement or renewal. The Tests shall be carried out in accordance with Clause 28.

30.8	Right of Access

Until the Final Certificate of Payment has been issued, the Contractor shall have the right of access to all parts of the Works and to records of the working and performance of the Works.

Such right of access shall be during the Employer's normal working hours at the Contractor's risk and cost. Access shall also be granted to any duly authorised representative of the Contractor whose name has been communicated in writing to the Engineer.

Subject to the Engineer's approval, the Contractor may also at his own risk and cost make any tests which he considers desirable.

30.9	Defects in Employer's and Engineer's Designs

The Contractor shall not be liable for any defects resulting from designs furnished or specified by the Employer or the Engineer.

30.10	Contractor to Search

The Contractor shall, if required by the Engineer in writing, search for the cause of any defect, under the direction of the Engineer. Unless the defect is one for which the Contractor is liable under this Clause, the cost of the work carried out by the Contractor in searching for the cause of the defect shall be added to the Contract Price.

30.11	Defects Liability Certificate

When the Defects Liability Period for the Works or any part thereof has expired and the Contractor has fulfilled all his obligations under the Contract for defects in the Works or that part, the Engineer shall issue within 28 days to the Employer and the Contractor a Defects Liability Certificate to that effect.

30.12	Exclusive Remedies

Except in the case of Gross Misconduct, the Employer's remedies under this Clause shall be in place of and to the exclusion of any other remedy in relation to defects whatsoever.

Variations

31.1	Engineer's Right to Vary

The Engineer may by Variation Order to the Contractor at any time before the Works are taken over, instruct the Contractor to alter, amend, omit, add to or otherwise vary any part of the Works.

The Contractor shall not vary or alter any of the Works, except in accordance with a Variation Order from the Engineer. The Contractor may, however, at any time propose variations of the Works to the Engineer.

31.2	Variation Order Procedure

Prior to any Variation Order under Sub-Clause 31.1 the Engineer shall notify the Contractor of the nature and form of such variation.

As soon as possible after having received such notice, the Contractor shall submit to the Engineer:

(a)a description of work, if any, to be performed and a programme for its execution, and

(b)the Contractor's proposals for any necessary modifications to the Programme according to Sub-Clause 26.1 ro to any of the Contractor’s obligations under the Contract, and

(c)the Contractor's proposals for adjustment to the Contract Price.

Following the receipt of the Contractor's submission the Engineer shall, after due consultation with the Employer and the Contractor, decide as soon as possible whether or not the variation shall be carried out.

If the Engineer decides that the variation shall be carried out, he shall issue a Variation Order clearly identified as such in accordance with the Contractor's submission or as modified by agreement. If the Engineer and the Contractor are unable to agree the adjustment of the Contract Price, the provisions of Sub-Clause 31.3 shall apply.

31.3	Disagreement on Adjustment of the Contract Price

If the Contractor and the Engineer are unable to agree on the adjustment of the Contract Price, the adjustment shall be determined in accordance with the rates specified in the Schedule of Prices.

If the rates contained in the Schedule of Price are not directly applicable to the specific work in question, suitable rates shall be established by the Engineer reflecting the level of pricing in the Schedule of Prices

Where rates are not contained in the said Schedule, the amount shall be such as is in all the circumstances reasonable. Due account shall be taken of any over-or under-recovery of overheads by the Contractor in consequence of the variation.

The Contractor shall also be entitled to be paid.

(a) the cost of any partial execution of the Works rendered useless by any such variation, and

(b) the cost of making necessary alterations to Plant already manufactured or in the course of manufacture or of any work done that has to be altered in consequence of such a variation, and

(c) any additional costs incurred by the Contractor by the disruption of the progress of the Works as detailed in the Programme, and

(d) the net effect of the Contractor's finance costs, including interest, caused by the variation.

The Engineer shall on this basis determine the rates or prices to enable on-account payment to be included in certificates of payment.

31.4	Contractor to Proceed

On receipt of a Variation Order, the Contractor shall forthwith proceed to carry out the variation and be bound to these Conditions in so doing as if such variation was stated in the Contract.

The work shall not be delayed pending the granting of an extension of the Time for Completion or an adjustment to the Contract Price under Sub-Clause 31.3.

31.5	Records of Costs

In any case where the Contractor is instructed to proceed with variation prior to the determination of the adjustment to the Contract Price in respect thereof the Contractor shall keep records of the cost of undertaking the variation and of time expended thereon. Such records shall be open to inspection by the Engineer at all reasonable times.

Ownership of Plant

32.1	Ownership of Plant

Plant to be supplied pursuant to the Contract shall become the property of the Employer at whichever is the earlier of the following times:

(a)when Plant is delivered to Site, or

(b)when by virtue of Sub-Clause 24.2 the Contractor becomes entitled to payment of the value of the Plant

Certificates and Payment

33.1	Terms of Payment

The terms of payment shall be as stated in the Preamble.

33.2	Method of Application

Unless otherwise specified in Part II applications by the Contractor for payment shall be made to the Engineer as follows:

(a)in respect of the progress of the Works accompanied by such evidence of the value of the work done as the Engineer may require, and

(b)in respect of Plant shipped and enroute to the Site identifying the Plant concerned and accompanied by such evidence of shipment and of payment of freight and insurance and by such other documents as the Engineer may require, and

(c)for additional payment in accordance with Clause 34.

Any other application for payment shall state the amounts claimed and the detailed particulars in respect of which the application is made.

33.3	Issue of Certificate of Payment

Within 14 days after receiving an application for payment which the Contractor was entitled to make the Engineer shall issue a Certificate of Payment to the Employer showing the amount due, with a copy to the Contractor.

A certificate of payment, other than the Final Certificate of Payment, shall not be withheld on account of:

(a)defects of a minor character which are not such as to affect the use of the Works, or

(b)any part of the payment applied for being disputed. In such case a certificate of payment for the undisputed amount shall be issued.

33.4	Corrections to Certificates of Payment

The Engineer may in any certificate of payment make any correction or modification that should properly be made in respect of any previous certificate.

33.5	Payment

Unless otherwise specified in Part II, the Employer shall pay the amount certified within 28 days from the date of issue of each certificate of payment to the Contractor at his principal place of business.

33.6	Delayed Payment

If payment of any sum payable under Sub-Clause 33.5 is delayed, the Contractor shall be entitled to receive interest on the amount unpaid during the period of delay. Unless otherwise stated in Part II the interest shall be at the annual rate three percentage points above the discount rate of the central bank in the Contractor's country. The Contractor shall be entitled to such payment without formal notice and without prejudice to any other right or remedy.

33.7	Remedies on Failure to Certify or Make Payment

The Contractor shall be entitled to stop the Works by giving 14 days’ notice to the Engineer and the Employer, if either:

(a)the Engineer fails to issue a certificate of payment upon proper application by the Contractor, or

(b)the Employer fails to make any payment as provided in this Clause.

The cost to the Contractor together with profit occasioned by the stoppage and the subsequent resumption of work, shall be added to the Contract Price.

The Contractor shall also be entitled to terminate the Contract by giving 28 days’ notice to the Engineer and the Employer in any case where the Engineer has failed to issue a certificate of payment upon proper application by the Contractor.

33.8	Payment by Measurement

For any part of the Works which is to be paid according to quantity supplied or work done, the provisions for measurement shall be stated in Part II.

33.9	Application for Final Certificate of Payment

The Contractor shall make application to the Engineer for the Final Certificate of Payment within 28 days after the issue of the Defect Liability Certificate, or if more than one, the last Defect Liability Certificate.

The application for the Final Certificate of Payment shall be accompanied by a final account prepared by the Contractor. The final account shall give full details of the value of all Plant supplied and work done under the Contract together with:

(a)such additions to or deductions from the Contract Price as have been agreed, and

(b)all claims for additional payment to which the Contractor may consider himself entitled.

33.10	Issue of Final Certificate of Payment

The Engineer shall issue to the Employer with a copy to the Contractor, the Final Certificate of Payment within 28 days after receiving an application in accordance with Sub-Clause 33.9.

If the Contractor has not applied for a Final Certificate of Payment within the time specified in Sub-Clause 33.9 the Engineer shall request the Contractor to do so within a further period of 28 days. If the Contractor fails to make such an application, the Engineer shall issue the Final Certificate of Payment for such amount as he deems correct.

33.11	Final Certificate of Payment Conclusive

A Final Certificate of Payment shall be conclusive evidence of the value of the Works, that the Works are in accordance with the Contract and that the Contractor has Particular

performed all his obligations under the Contract.

Payment of the amount certified in the Final Certificate of Payment shall be conclusive evidence that the Employer has performed all his obligations under the Contract.

A Final Certificate of Payment or payment shall not be conclusive:

(a)to the extent that fraud or dishonesty relates to or affects any matter dealt with in the certificate, or

(b)if any arbitration or court proceedings under the Contract have been commenced by either party before the expiry of 84 days after the issue of the Final Certificate of Payment.

Claims

34.1	Procedure

In any case where under these Conditions there are circumstances which the Contractor considers entitle him to claim additional payment, the Contractor shall:

(a)if he intends to make any claim for additional payment give to the Engineer notice of his intention to make such claim within 28 days after the said circumstances became known to the Contractor stating the reasons for his claim,

and

(b)as soon as reasonably practical after the date of such notice submit to the Engineer full and detailed particulars of his claim but not later than 182 days after such notice unless otherwise agreed by the Engineer. In any event such particulars shall be submitted no later than the application for the Final Certificate of Payment. The Contractor shall thereafter promptly submit such further particulars as the Engineer may reasonably require to assess the validity of the claim

34.2	Assessment

When the Engineer has received full and detailed particulars of the Contractor's claim in accordance with Sub-Clause 34.1 and such further particulars as he may reasonably have required he shall after due consultation with the Employer and the Contractor determine whether the Contractor is entitled to additional payment and notify the parties accordingly.

The Engineer may reject any claim for additional payment which does not comply with the requirements of Sub-Clause 34.1.

Foreign Currency and Rates of Exchange

35.1	Payment in Foreign Currencies

Arrangements for payment in foreign currencies shall be as stated in the Preamble.

35.2	Currency Restrictions

The Employer shall reimburse the Contractor for any loss arising from:

(a)currency restrictions, and

(b)restrictions on the transfer of currency in which the Contractor is to be paid which are imposed by the government or authorised agency of the government of the country from which any payments under the Contract are to be made.

This Sub-Clause only applies to restrictions imposed after the date 28 days prior to the latest date for submission of tenders for the Works.

35.3	Rates of Exchange

Where the Contract provides for payment in Foreign Currency the rates of exchange between the currencies shall be fixed for the purpose of the Contract and shall be as stated in the Preamble.

If such rates of exchange are not stated in the Preamble the rates to be used shall be those quoted by the central bank of the country whose currency is to be sold 28 days or the nearest day thereto prior to the latest date for submission of tenders for the Works.

Provisional Sums

36.1	Use of Provisional Sums

A Provisional Sum shall only be used, in whole or in part in accordance with the Engineer's instructions.

The total sum paid to the Contractor shall include only such amounts in respect of work, supplies or services to which such Provisional Sums relate as the Engineer shall have instructed.

36.2	Ordering Work against Provisional Sums

In respect of every Provisional Sum the Engineer may after due consultation with the Employer and the Contractor order:

(a)work to be executed, including goods, materials or services to be supplied by the Contractor. The value of such work executed, determined in accordance with Clause 31, shall be paid to the Contractor in accordance with Clause 33, and

(b)goods and materials to be purchased by the Contractor, for which payment will be made in accordance with Sub-Clause 36.4.

36.3	Invoices and Receipts

The Contractor shall, when required by the Engineer, produce quotations, invoices, vouchers and accounts or receipts in connection with expenditure in respect of Provisional Sums.

36.4	Payment against Provisional Sums

For all work executed or goods, materials or services supplied or purchased by the Contractor under Sub-Clause 36.2(b), there shall be included in the sums paid to the Contractor:

(a)the actual price paid or due to be paid by the Contractor, and

(b)in respect of all other charges and profit, a percentage of the actual price paid or due to be paid. Such percentage shall be as stated in the Preamble.

Risk and Responsibility

37.1	Allocation of Risk and Responsibility

The Risks of loss of or damage to physical property and of death and personal injury which arise in consequence of the performance of the Contract shall be allocated between the Employer and the Contractor as follows:

(a) the Employer: The Employer’s Risks as specified in Sub-Clause 37.2

(b) the Contractor: The Contractor's Risks as specified in Sub-Clause 37.3.

37.2	Employer's Risks

The Employer's Risks are:

(a) war and hostilities (whether war be declared or not), invasion, act of foreign enemies;

(b)	rebellion, revolution, insurrection, military or usurped power or civil war insofar as it relates to the country in which the Works are located or countries through which plant must be transported;

(c)	ionizing radiation or contamination by radio-activity from any nuclear fuel, or from any nuclear waste from the combustion of nuclear fuel, radio-active toxic explosives or other hazardous properties of any explosive nuclear assembly or nuclear components thereof;

(d)	pressure waves caused by aircraft travelling at sonic or supersonic speed;

(e)	riot, commotion or disorder, unless solely restricted to the employees of the Contractor or of his Subcontractors;

(f)	use or occupation of the Works or any part thereof by the Employer;

(g)	fault, error, defect or omission in the design of any part of the Works by the Engineer, Employer or those for whom the Employer is responsible;

(h)	the use or occupation of the Site by the Works or any part thereof, or for the purposes of the Contract; or interference, whether temporary or permanent with any right of way, light, air or water or with any easement, wayleaves or right of a similar nature which is the inevitable result of the construction of the Works in accordance with the Contract;

(i)	the right of the Employer to construct the Works or any part thereof on, over, under, in or through any land;

(j)	damage (other than that resulting from the Contractor's method of construction) which is the inevitable result of the construction of the Works in accordance with the Contract;

(k)	the act, neglect or omission or breach of contract or of statutory duty of the Engineer, the Employer or other contractors engaged by the Employer or of their respective employees or agents;

and all risks which an experienced contractor could not have foreseen or, if foreseeable, against which measures to prevent loss, damage or injury from occurring could not reasonably have been taken by such contractor.

37.3	Contractor's Risks

The Contractor's Risks are all risks other than those identified as the Employer's Risks.

Care of the Works and Passing of Risk

38.1	Contractor's Responsibility for the Care of the Works

The Contractor shall be responsible for the care of the Works or any Section thereof from the Commencement until the Risk Transfer Date applicable thereto under Sub-Clause 38.2.

The Contractor shall also be responsible for the care of any part of the Works upon which any outstanding work is being performed by the Contractor during the Defects Liability Period until completion of such outstanding work.

38.2	Risk Transfer Date

The Risk Transfer Date in relation to the Works or a Section thereof is the earliest of either:

(a)the date of issue of the Taking-Over Certificate, or

(b)the date when the Engineer is deemed to have issued the Taking Certificate or the Works are deemed to have been taken over in accordance with Clause 29, or

(c)the date of expiry of the notice of termination when the Contract is terminated by the Employer or the Contractor in accordance with these Conditions.

39.1	Passing of Risk of Loss of or Damage to the Works

The risk of loss of or damage to the Works or any Section thereof shall pass from the Contractor to the Employer on the Risk Transfer Date applicable thereto.

39.2	Loss or Damage Before Risk Transfer Date

Loss of or damage to the Works or any Section thereof occurring before the Risk Transfer Date shall:

(a)to the extent caused by any of the Contractor's Risks, be made good forthwith by the Contractor at his own cost, and

(b)to the extent caused by any of the Employer's Risks, be made good by the Contractor at the Employer's expense if so required by the Engineer within 28 days after the occurrence of the loss or damage. The price for making good such loss and damage shall be in all circumstances reasonable and shall be agreed by the Employer and the Contractor, or in the absence of agreement, shall be fixed by arbitration under Clause 50.

39.3	Loss or Damage After Risk Transfer Date

After the Risk Transfer Date, the Contractor's liability in respect of loss of or damage to any part of the Works shall, except in the case of Gross Misconduct, be limited:

(a)to the fulfillment of the Contractor's obligations under Clause 30 in respect of defects therein, and

(b)to making good forthwith loss or damage caused by the Contractor during the Defects Liability Period.

Damage to Property and Injury to Persons

40.1	Contractor's Liability

Except as provided under Sub-Clause 41.1, the Contractor shall be liable for and shall indemnify the Employer against all losses, expenses and claims in respect of any loss of or damage to physical property (other than the Works), death or personal injury occurring before the issue of the last Defects Liability Certificate to the extent caused by:

(a)defective design, material or workmanship of the Contractor, or

(b)negligence or breach of statutory duty of the Contractor, his Subcontractors or their respective employees and agents.

40.2	Employer's Liability

The Employer shall be liable for and shall indemnify the Contractor against all losses, expenses or claims in respect of loss of or damage to any physical property or of death or personal injury whenever occurring, to the extent caused by any of the Employer's Risks.

41.1	Accidents

The Contractor shall be liable for and shall indemnify the Employer against all losses, expenses or claims arising in connection with the death of or injury to any person employed by the Contractor or his Subcontractors for the purposes of the Works, unless caused by any acts or defaults of the Engineer, the Employer, or other contractors engaged by the Employer or by their respective employees or agents. In the latter cases the Employer shall be liable for and shall indemnify the Contractor against all losses, expenses and claims arising in connection therewith.

Limitations of Liability

42.1	Liability for Indirect or Consequential Damage

Neither party shall be liable to the other for any loss of profit, loss of use, loss of production, loss of contracts or for any other indirect or consequential damage that may be suffered by the other, except:

(a)as expressly provided in Clause 27, and

(b)those provisions of these Conditions whereby the Contractor is expressly entitled to receive profit.

42.2	Maximum Liability

The liability of the Contractor to the Employer under these Conditions shall in no case exceed the sum stated in the Preamble or, if no such sum is stated, the Contract Price.

42.3	Liability after Expiration of Defects Liability Period

The Contractor shall have no liability to the Employer for any loss of or damage to the Employer's physical property which occurs after the expiration of the Defects Liability Period unless caused by Gross Misconduct of the Contractor.

42.4	Exclusive Remedies

The Employer and the Contractor intend that their respective rights, obligations and liabilities as provided for in these Conditions shall alone govern their rights under the Contract and in relation to the Works.

Accordingly, the remedies provided under the contract in respect of or in consequence of:

(a)any breach of contract, or

(b)any negligent act or omission, or

(c)death or personal injury, or

(d)loss or damage to any property

are, save in the case of Gross Misconduct, to be to the exclusion of any other remedy that either may have against the other under the law governing the Contract or otherwise.

42.5	Mitigation of Loss of Damage

In all cases the party claiming a breach of Contract or a right to be indemnified in accordance with the Contract shall be obliged to take all reasonable measures to mitigate loss or damage which has occurred or may occur.

42.6	Foreseen Damage

Where either the Employer or the Contractor is liable in damages to the other these shall not exceed the damage which the party in default could reasonably have foreseen at the date of the Contract.

Insurance

43.1	The Works

The Contractor shall insure the Works in the joint names of the Contractor and the Employer to their full replacement value with deductible limits not exceeding those stated in the Preamble.

(a)from the Commencement Date until the Risk Transfer Date against any loss or damage caused by any of the Contractor's Risks and any other risks specified in the Preamble, and

(b)during the Defects Liability period against any loss or damage which is caused either:

(i)by the Contractor in completing any outstanding work or complying with his obligations under Clause 30, or

(ii)by any of the Contractor's Risks which occurred prior to the Risks Transfer Date.

43.2	Contractor's Equipment

The Contractor shall insure Contractor's Equipment for its full replacement value whilst in transit to the Site, from commencement of loading until completion of unloading at the Site and while on the Site against all loss or damage caused by any of the Contractor's Risks.

43.3	Third Party Liability

The Contractor shall insure against liability to third parties for any death or personal injury and loss of or damage to any physical property arising out of the performance of the Contract and occurring before the issue of the last Defects Liability Certificate.

Such insurance shall be effected before the Contractor begins any work on the Site The insurance shall be for not less than the amount specified in the Preamble.

43.4	Employees

The Contractor shall insure and maintain insurance against his liability under Sub-Clause 41.1.

43.5	General Requirements of Insurance Policies

The Contractor shall:

(a)whenever required by the Employer produce the policies or certificates of any insurance which he is required to effect under the Contract together with receipts for the premiums,

(b)effect all insurances for which he is responsible with an insurer and in terms approved by the Employer, and

(c)make no material alterations to the terms of any insurance without the Employer's approval. If an insurer makes any material alteration to the terms the Contractor shall forthwith notify the Employer, and

(d)in all respect comply with any conditions stipulated in the insurance policies which he is required to place under the Contract.

43.6	Permitted Exclusions from Insurance Policies

The insurance cover effected by the Contractor may exclude any of the following:

(a)the cost of making good any part of the Works which is defective or otherwise does not comply with the Contract provided that it does not exclude the cost of making good any loss or damage to any other part of the Works attributable to such defect or non-compliance,

(b)indirect or consequential loss of damage including any reductions in the Contract Price for delay,

(c)wear and tear, shortages and theft,

(d)risks relating to vehicles for which third party or other insurance is required by law.

43.7	Remedies on the Contractor's Failure to Insure

If the Contractor fails to produce evidence of insurance cover as stated in Sub-Clause 43.5 (a) then the Employer may effect and keep in force such insurance. Premiums paid by the Employer for this purpose shall be deducted from the Contract Price.

43.8	Amounts not Recovered

Any amounts not recovered from the insurers shall be borne by the Employer or Contractor in accordance with their responsibilities under Clause 37.

Force Majeure

44.1	Definition of Force Majeure

Force Majeure means any circumstances beyond the control of the parties, including but not limited to:

(a)war and other hostilities, (whether war be declared or not), invasion, act of foreign enemies, mobilization, requisition or embargo;

(b)ionizing radiation or contamination by radio-activity from any nuclear fuel or from any nuclear waste from the combustion of nuclear fuel, radio-active toxic explosives, or other hazardous properties of any explosive nuclear assembly or nuclear components thereof;

(c)rebellion, revolution, insurrection, military or usurped power and civil war;

(d)riot, commotion or disorder, except where solely restricted to employees of the Contractor.

44.2	Effect of Force Majeure

Neither party shall be considered to be in default or in breach of his obligations under the Contract to the extent that performance of such obligations is prevented by any circumstances of Force Majeure which arise after the date of the Letter of Acceptance or the date when the Contract becomes effective, whichever is the earlier.

44.3	Notice of Occurrence

If either party considers that any circumstances of Force Majeure have occurred which may affect performance of his obligations he shall promptly notify the other party and the Engineer thereof.

44.4	Performance to Continue

Upon the occurrence of any circumstances of Force Majeure the Contractor shall endeavor to continue to perform his obligations under the Contract so far as reasonably practicable. The Contractor shall notify the Engineer of the steps he proposes to take including any reasonable alternative means for performance which is not prevented by Force Majeure. The Contractor shall not take any such steps unless directed so to do by the Engineer.

44.5	Additional Costs caused by Force Majeure

If the Contractor incurs additional costs in complying with the Engineer's directions under Sub-Clause 44.4, the amount thereof shall be certified by the Engineer and added to the Contract Price.

44.6	Damage Caused by Force Majeure

If in consequence of Force Majeure the Works shall suffer loss or damage the Contractor shall be entitled to have the value of the work done, without regard to the loss or damage that has occurred, included in a Certificate of Payment.

44.7	Termination in Consequence of Force Majeure

If circumstances of Force Majeure have occurred and shall continue for a period of 182 days then, notwithstanding that the Contractor may by reason thereof have been granted an extension of Time for Completion of the Works, either party shall be entitled to serve upon the other 28 days' notice to terminate the Contract. If at the expiry of the period of 28 days Force Majeure shall still continue the Contract shall terminate.

44.8	Payment on Termination for Force Majeure

If the Contract is terminated under Sub-Clause 44.7 the Contractor shall be paid the value of the work done.

The contractor shall also be entitled to receive:

(a)the amounts payable in respect of any preliminary items so far as the work or service comprised therein has been carried out and a proper proportion of any such item in which the work or service comprised has only been partially carried out,

(b)the cost of materials or goods ordered for the Works or for use in connection with the Works which have been delivered to the Contractor or of which the Contractor is legally liable to accept delivery. Such materials or goods shall become the property of and be at the risk of the Employer when paid for by the Employer and the Contractor shall place the same at the Employer's disposal,

(c)the amount of any other expenditure which in the circumstances was reasonably incurred by the Contractor in the expectation of completing the whole of the Works,

(d)the reasonable cost of removal of Contractor's Equipment from the Site and the return thereof to the Contractor's works in his country or to any other destination at no greater cost, and

(e)the reasonable cost of repatriation of the Contractor's staff and workmen employed wholly in connection with the Works at the date of such termination.

44.9	Release from Performance

If circumstances of Force Majeure occur and in consequence thereof under the law governing the Contract the parties are released from further performance of the Contract, the sum payable by the Employer to the Contractor shall be the same as that which would have been payable under Sub-Clause 44.8 if the Contract had been terminated under Sub-Clause 44.7.

44.10	Force Majeure Affecting Engineer's Duties

The provisions of Clause 44 shall also apply in circumstances where the Engineer is prevented from performing any of his duties under the Contract by reason of Force Majeure.

Default

45.1	Notice of Default

If the Contractor is not executing the Works in accordance with the Contract or is neglecting to perform his obligations thereunder so as seriously to affect the carrying out of the Works, the Engineer may give notice to the Contractor requiring him to make good such failure or neglect.

45.2	Contractor's Default

If the Contractor:

(a) has failed to comply within a reasonable time with a notice under Sub-Clause 45.1, or

(b)	assigns the Contract or subcontracts the whole of the Works without the Employer's written consent, or

(c)	becomes bankrupt or insolvent, has a receiving order made against him or compounds with his creditors, or carries on business under a receiver, trustee or manager for the benefit of his creditors or goes into liquidation,

the Employer may, after having given 7 days’ notice to the Contractor, terminate the Contract and expel the Contractor from the Site.

Any such expulsion and termination shall be without prejudice to any other rights or powers of the Employer, the Engineer or the Contractor under the Contract.

The Employer may upon such termination complete the Works himself or by any other contractor.

45.3	Valuation at Date of Termination

The Engineer shall, as soon as possible after such termination, certify the value of the Works and all sums then due to the Contractor as at the date of termination in accordance with Clause 33.

45.4	Payment after Termination

The Employer shall not be liable to make any further payments to the Contractor until the Works have been completed. When the Works are so complete, the Employers shall be entitled to recover from the Contractor the extra costs, if any, of completing the Works after allowing for any sum due to the Contractor under Sub-Clause 45.3. If there is no such extra cost the Employer shall pay any balance due to the Contractor.

45.5	Effect on Liability for Delay

The Contractor's liability under Clause 27 shall immediately cease when the Employer expels him from the Site without prejudice to any liability thereunder that may have already occurred.

46.1	Employer's Default

The Contractor may, by giving 14 days’ notice to the Employer and the Engineer, terminate the Contract if the Employer:

(a)fails to pay the Contractor the amount due under any certificate of the Engineer within 28 days after the amount became payable, or

(b)interferes with or obstructs the issue of any certificate of the Engineer, or

(c)becomes bankrupt or insolvent, has a receiving order made against him, compounds with his creditors, or carries on business under a receiver, trustee or manager for the benefit of his creditors or goes into liquidation, or goes into liquidation, or

(d)consistently fails to meet his contractual obligations, or

(e)appoints, a person to act with or in replacement of the Engineer without the Contractor's consent.

Any such termination shall be without prejudice to any other rights of the Contractor under the Contract.

46.2	Removal of Contractor's Equipment

On such termination, the Contractor shall be entitled to remove immediately all Contractor's Equipment which is on the Site.

46.3	Payment on Termination for Employer's Default

In the event of such termination the Employer shall pay the Contractor an amount calculated in accordance with Sub-Clause 44.8.

The Employer shall pay in addition the amount of any loss or damage, including loss of profit which the Contractor may have suffered in consequence of termination. The additional amount shall, however, not exceed the limit specified in the Preamble.

Change in Cost and Legislation

47.1	Labour, Materials and Transport

Where the Contract Price is to be adjusted for changes in the cost of labour, materials, transport or other costs of execution of the Works, the method for calculating such adjustment shall be specified in the Preamble.

When calculating the adjustment, no account shall be taken of any increased cost which results from the Contractor's default or negligence.

47.2	Statutory and Other Regulations

The Contract Price shall be adjusted to take account of any increase or decrease in cost resulting from changes in legislation of the country where the Site is located or in its generally accepted interpretation.

Legislation means any law, order, regulation or bye-law having the force of law, which affects the Contractor in the performance of his obligations under the Contract, made after the date 28 days prior to the latest date for submission of tenders for the Works.

The Engineer shall certify the amount of the resulting increase or decrease in cost, which shall be added to or deducted from the Contract Price.

Customs

48.1	Customs and Import Duties

Unless otherwise stated in Part II the Employer shall pay all customs, import duties and taxes in consequence of the importation of Plant. If the Contractor is required to pay such customs, import duties and taxes, the Employer shall reimburse the amount thereof.

48.2	Clearance through Customs

The Employer shall assist the Contractor in obtaining clearance through the customs of all Plant and Contractor's Equipment and in procuring any necessary government consent to the re-export of Contractor's Equipment when it is removed from the Site.

Notices

49.1	Notices to Contractor

All certificates, notices or written orders to be given to the Contractor by the Employer or the Engineer under these Conditions shall be sent by airmail post, cable, telex or facsimile transmission to or left at the Contractor's principal place of business or such other address as the Contractor shall nominate for that purpose, or may be handed over to the Contractor's representative.

49.2	Notice to Employer and Engineer

Any notice to be given to the Employer or to the Engineer under these Conditions shall be sent by airmail post, cable, telex or facsimile transmission to or left at the respective addresses nominated for that purpose in the Preamble, or handed over to the Engineer's or the Employer's representative authorized to receive it.

B 	49.3	Minutes of Meetings

Instructions or notices to the Contractor and notices from the Contractor to the Engineer or the Employer recorded in a minute or protocol signed by the authorized representatives of the giver and recipient of such notice or instruction shall be valid notice or instruction for the purposes of the Contract.

Disputes and Arbitration

50.1	Disputes concerning Engineer's Decisions

If either party is dissatisfied with a decision or instruction of the Engineer as confirmed, reversed or varied in accordance with Clause 2 he may refer the matter to arbitration pursuant to Sub-Clause 50.2.

Unless the dissatisfied party has notified the other party and the Engineer within 56 days of such decision or instruction of his intention to refer the matter to arbitration, he shall be deemed to have accepted the decision as final.

Reference to arbitration shall not relieve the Contractor of his obligation to proceed with the Works in accordance with the Engineer's decision or instruction, nor relieve the Employer of any of his obligations under the Contract.

The Contractor shall in any such arbitration be at liberty to rely on reasons additional to the reasons stated in the notice given under Sub-Clause 2.7.

50.2	Arbitration

If at any time any question, dispute or difference shall arise between the Employer and the Contractor in connection with or arising out of the Contract or the carrying out of the Works either party shall be entitled to refer the matter to be finally settled by arbitration in accordance with the Rules of Conciliation and Arbitration of the International Chamber of Commerce by one or more arbitrators appointed in accordance with those Rules, or by arbitration in accordance with such other rules as are specified in Part II.

The Arbitrators(s) shall have full power to open up, review and revise:

(a)any decision or instruction of the Engineer referred to arbitration pursuant to Sub-Clause 50.1, and

(b)any certificate of the Engineer related to the dispute.

50.3	Works to Continue

Performance of the Contract shall continue during arbitration proceedings unless the Employer shall order suspension. If any such suspension is ordered the reasonable costs incurred by the Contractor and occasioned thereby shall be added to the Contract Price.

No payments due or payable by the Employer shall be withheld on account of pending reference to arbitration.

50.4	Time Limit for Arbitration

Formal notice of arbitration must be given to the other party, and where required to the appropriate arbitration body, no later than 84 days after the issue of the Final Certificate of Payment

Law and Procedure

51.1	Applicable Law

The law which is to apply to the Contract and under which the Contract is to be construed is stated in the Preamble.

51.2	Procedural Law

The law governing the procedure and administration of any arbitration instituted pursuant to Clause 50 is stated in the Preamble.

51.3	Language

The language and place of the arbitration are stated in the Preamble.

INDEX								Clause	Page

Access, authority for	14.7

Access, not exclusive	17.1

Access, Right of Contractor	30.8

Access to and possession of the Site	17.1

Accident or injury to Contractor’s employees	41.1

Additional cost caused by Force Majeure	44.5

Additional payment, claims procedure	34.1

Address for Notice, Contractor	49.1

Address for Notice, Employer	49.2

Address for Notice, Engineer	49.2

Ambiguities and Discrepancies	 5.4

Applicable Law	51.1

Application for Certificates of Payment	33.2

Application for Final Certificate of Payment 	33.9

Approved Contractor’s Drawings	 6.3

Arbitration, reference to	50.2

Arbitration, performance of Contract to continue	50.3

Arbitration, time limit for formal notice	50.4

Assignment	 3.1

Assistance with local regulations	17.2

Bankruptcy of Contractor	45.2 (c)

Bankruptcy of Employer	46.1

Care of the Works	38.1

Certificate of Payment, application for final	33.9

Certificate of Payment, corrections to	33.4

Certificate of Payment, final, conclusive	33.11

Certificate of Payment, issue of	33.3

Certificate of Payment, method of application	33.2

Certificate of Testing	20.5

Certificate, Taking-Over	29.2

Changes in cost, labour materials and transport	47.1

Changes in statutory and other regulations	47.2

Civil works on Site	17.3

Claims for additional payment, assessment	34.2

Claims for additional payment, procedure	34.1

Claims in respect of Patent Rights	16.2

Claims under Performance Security	10.3

Clearance of Site, periodically and on Completion	14.5

Confirmation in writing	2.6

Communications, day to day 	5.2

Completion, clearance of Site on	14.5

Completion, delay in	27.1

Completion, delays by Subcontractors	26.2

Completion, earlier	26.3

Completion, extension of time for	26.1

INDEX

Completion, prolonged delay	27.2

Completion, time for	25.1

Completion, facilities for Tests	28.4

Completion, consequences of failure to pass Tests	28.7

Compliance with laws	15.2

Compliance with Statutes and Regulations	15.1

Consents and Wayleaves	17.4

Consequences of disapproval of Contractor’s Drawings	6.2

Consequential Damage, liability for	42.1

Contract Agreement	9.1

Contract documents, priority of 	5.3

Contractor, General Obligations	8.1

Contractor’s, Default	45.2

Contractor’s Drawings	6.1

Contractor’s Drawings, additional copies	6.1

Contractor’s Drawings, consequences of disapproval of 	6.2

Contractor’s Drawings, inspection of	6.4

Contractor’s Drawings, no deviation	6.3

Contractor’s employees, objections to	13.2

Contractor’s Equipment	14.1

Contractor’s Equipment, exclusive use of	14.1

Contractor’s Equipment, insurance of	43.2

Contractor’s Equipment, removal of	46.2

Contractor’s Liability	40.1

Contractor’s opportunities for other	14.6

Contractor’s representative	13.1

Contractor’s responsibility for the Care of the Works	38.1

Contractor’s Risks	37.3

Contractor to proceed	31.4

Contract Price, sufficiency of	11.2

Contractor to search	30.10

Contractor’s use of Employer’s Drawings	6.8

Corrections to Certificates of Payment	33.4

Costs, overhead charges and profit	1.6

Costs, records of	31.5

Covering up work	19.2

Currency restrictions	35.2

Customs and import duties	48.1

Customs, clearance through	48.2

Damage after Risk Transfer Date	39.3

Damage before Risk Transfer Date	39.2

Damage caused by Force Majeure	44.6

Damage, liability for indirect or consequential	42.1

Damage, foreseen 	42.6

Damage to property, Contractor’s Liability	40.1

Damage to property, Employer’s Liability	40.2

INDEX

Damage to the Works, passing of risk	39.1

Data, Site	11.1

Dates, for Inspection and Testing	20.3

Day to Day communications	5.2

Default of Contractor	45.2

Default of Employer	46.1

Defective work, removal of	30.6

Defect failure to remedy	30.5

Defects in Employer’s and Engineer’s Designs	30.9

Defects Liability Certificate 	30.11

Defects Liability Good	30.1

Defects Liability Period, extension of	30.4

Defects, making Period	30.2

Defects, notice of	30.3

Definitions	1.1

Delayed payment	33.6

Delayed Tests	28.3

Delay in Completion	27.1

Delay, prolonged	27.2

Delays by Subcontractors	26.2

Delivery of Plant, permission for	22.1

Design of Plant	8.1

Discrepancies and Ambiguities	5.4

Disagreement as to results of Tests	28.6

Disagreement on adjustment of the Contract Price	31.3

Disapproval of Contractor’s Drawings, consequences of	6.2

Disputes concerning Engineer’s Decisions	2.7/50.1

Documents mutually explanatory	5.4

Drawings, Contractor’s	6.1

Earlier Completion	26.3

Effect on liability for delay	45.5

Electricity , Water and Gas	14.3

Employer/Engineer, errors by	7.2

Employer/Engineer, notices to	49.2

Employer’s Default	46.1

Employer’s Default, payment on termination for 	46.3

Employer’s Equipment	14.4

Employer’s right to maintain insurance cover	43.7

Employer’s Risks	37.2

Employer’s use of Contractor’s Drawings	6.7

Employer’s Warranty for Patent Rights	16.3

Engagement of Labour	18.1

Engineer/Employer, notice to	49.2

Engineer Decisions and Instructions	2.5

Engineer Decisions, disputes concerning	2.7/50.1

INDEX

Engineer’s Duties	2.1

Engineer’s Power to Delegate	2.3

Engineer, Replacement of	2.8

Engineer’s Representative	2.2

Engineer’s Right to Vary	31.1

Engineer to act impartially	2.4

Equipment, Contractor’s	14.1

Equipment, Contractor’s removal on default of Employer	46.2

Equipment, Employer’s	14.4

Erection Information to be provided by Contractor	6.5

Errors by Employer/Engineer	7.2

Errors in Contractor’s Drawings	7.1

Exchange Rates	35.3

Exclusive Remedies 	30.12

Execution, manner of 	19.1

Extension of Defects Liability Period	30.4

Extension of Time for Completion	26.1

Facilities for Testing	20.4

Facilities for Tests on Completion	28.4

Failure to certify, remedies on 	33.7

Failure to insure	43.7

Failure to make payment, remedies	33.7

Failure to pass Tests on Completion, consequences of	28.7

Fencing, lighting and guarding	14.2

Final Certificate of Payment, application for	33.9

Final Certificate of Payment conclusive	33.11

Final Certificate of Payment, issue of	33.10

Force Majeure, additional costs caused by	44.5

Force Majeure affecting Engineer’s Duties	44.10

Force Majeure, damage caused by	44.6

Force Majeure, definition of	44.1

Force Majeure, effect of	44.3

Force Majeure, notice of occurrence	42.2

Force Majeure, payment on termination for	44.8

Force Majeure, performance to continue	44.4

Force Majeure, release from performance 	44.9

Force Majeure, termination in consequence of	44.7

Foreign currencies, payment in	35.1

Foreseen damages	42.6

Gas, Electricity and Water	14.3

General Obligations of the Contractor	8.1

Guarding, Fencing and Lighting	14.2

Heading and Titles	1.2

Hours of work	18.3

Hours of work, restriction of	18.4

INDEX

Import Duties and Customs	48.1

Import Permits and Licences	17.5

Independent Inspection	20.1

Indirect or Consequential Damage, liability for	42.1

Information for Import Permits and Licences	14.8

Inspection and Testing, dates for	20.3

Inspection and Testing during manufacture	20.2

Inspection of Contractor’s Drawings	6.4

Insurance, Contractor’s Equipment	43.2

Insurance of Employees	43.4

Insurance of Works	43.1

Insurance Policies, general requirements	43.5

Insurance Policies, permitted exclusions	43.6

Insurance, Third Party Liability	43.3

Interference with Tests on Completion	29.4

Interpretation	1.3

Invoices and Receipts - Provisional Sums	36.3

Issue of Certificate of Payment	33.3

Issue of Final Certificate of Payment	33.10

Labour, changes in cost and legislation	47.1

Labour, engagement of	18.1

Labour, restriction of working hours	18.4

Labour, returns of	18.2

Labour, working hours	18.3

Language, for arbitration	51.3

Language, ruling	5.1

Law, applicable	51.1

Law, procedural	51.2

Law, compliance with	15.2

Liability after expiration of Defect Liability Period	42.3

Liability for Damage to Property and Injury to Persons, the Contractor	40.1

Liability for Damage to Property and Injury to Persons, the Employer	40.2

Liability for Indirect or Consequential Damage	42.1

Liability, maximum	42.2

Liability, Third Party Insurance	43.3

Licences and Import Permits	17.5

Local Regulations, assistance with	17.2

Loss or Damage after Risk Transfer Date	39.3

Loss or Damage before Risk Transfer Date	39.2

Loss or Damage, mitigation of 	42.5

Loss or Damage to the Works, passing of risk	39.1

Maintenance and Operation Manual	6.6

Making good Defects	30.2

Manner of Execution	19.1

Manufacturer, Inspection and Testing during	20.2

INDEX

Manufacture of Plant	8.1

Manufacturing Drawings	6.9

Materials, Changes, in Cost and Legislation	47.1

Employer’s Liability	42.2

Measurement, payment by	33.8

Method of application for Certificates of Payment	33.2

Minutes of Meeting	49.3

Mitigation of Loss or Damage	42.5

Notice of Default	45.1

Notice of Defects	30.3

Notice of Occurrence, Force Majeure	44.3

Notice of Tests	28.1

Notices, Consents and Approvals	1.5

Notices to Contractor	49.1

Notices to Employer/Engineer	49.2

Objection to Contractor’s Employees	13.2

Obligations of the Contractor, General	8.1

Obligations of the Contractor, Setting Out	8.2

Operation and Maintenance Manuals	6.6

Opportunities for Other Contractors	14.6

Order to suspend work	23.1

Ordering Work against Provisional Sums	36.2

Overhead Charges	1.6

Ownership of Plant	32.1

Patent Rights, Claims in respect of	16.2

Patent Rights, Employer’s Warranty for	16.3

Patent Rights, Indemnification 	16.1

Payment	33.5

Payment by Measurement	33.8

Payment, Application for Final Certificate	33.9

Payment Certificate, corrections to	33.4

Payment Certificate, issue of	33.3

Payment, delayed	33.6

Payment, Final Certificate conclusive	33.11

Payment, issue of Final Certificate	33.10

Payment, method of application for 	33.2

Payment on Suspension 	24.2

Payment, remedies on failure to certify or make payment	33.7

Payment, terms of	33.1

Performance Security	10.1

Performance Security, claims under	10.3

Period of Validity, performance Security	10.2

Permits to Work	17.5

Physical Conditions	11.3

Plant, permission to deliver	22.1

INDEX

Plant, rejection	21.1

Plant, ownership	32.2

Possession of the Site, access to and	17.1

Priority of Contract Documents	5.3

Profit	1.6

Programme, alterations to 	12.2

Programme, revisions of	12.3

Programme to be furnished 	12.1

Prolonged delay	27.2

Prolonged Suspension	24.3

Provisional Sums, ordering work	36.2

Provisional Sums, payment against	36.4

Provisional Sums, use of	36.1

Purchase of Materials	4.1

Rates of Exchange 	35.3

Receipts and Invoices	36.3

Regulations, assistance with Local	17.2

Regulations, Statutes, compliance with	15.1

Regulations, Statutory and Others	47.2

Rejection of Plant	21.1

Remedies on failure to insure	43.7

Remedy of Contractor or Employer’s Default	46.1

Removal of Contractor’s Equipment	14.1

Removal of Contractor’s Equipment of Employer’s Default	46.2

Restriction, currency	35.2

Restriction of Working Hours	18.4

Resumption of Work	24.4

Retesting 	28.5

Returns of Labour	18.2

Rights, Patent	16.1

Rights, Patent, claims in respect of	16.2

Rights, Patent, Employer’s Warranty	16..3

Risks and Responsibility, allocation of	37.1

Risks of War and Other Hostilities	44.1

Risk transfer date	38.2

Safety, precautions on Site	14.2

Samples and Models	6.1

Setting Out	8.2

Settlement of Disputes - Arbitration	50.2

Singular and plural	1.3

Site, Access to and possession of	17.1

Site, Clearance of	14.5

Site Data	11.1

Statutes, Regulations, etc, compliance with	15.1

INDEX

Statutory and Other Regulations, changes in	47.2

Storage of Delayed Plant	23.1

Subcontracting	4.1

Subcontractors, responsibility of Contractor	4.1

Sufficiency of Contract Price	11.2

Supply of Water, Electricity and Gas	14.3

Suspension of Works	23.1

Suspension, Cost of	24.1

Suspension, payment in event of	24.2

Suspension, prolonged	24.3

Suspension, resumption of work	24.4

Taking Over	23.1

Taking - Over Certificate	29.2

Taking over, use before	29.3

Termination due to Contractor’s Default	45.2

Termination due to Employer’s Default	46.1

Termination in consequence of Force Majeure	44.7

Termination on Employer’s failure to make payment	33.7

Termination on Engineer’s failure to certify	33.7

Terms of Payment	33.1

Test Certificate	28.9

Testing and Inspection dates for	20.3

Testing and Inspection during manufacture	20.2

Testing, Certificate of 	20.5

Testing, Facilities for	20.4

Tests on completion, allowance for use	28.8

Tests on Completion, consequences of failure to pass	28.7

Tests on Completion, delayed	28.3

Tests on Completion, facilities for	28.4

Tests on Completion, further tests	30.7

Tests on Completion, notice of 	28.1

Tests on Completion, time for	28.2

Third Party Insurance	43.3

Time for Completion	25.1

Time for Completion - Extension of 	26.1

Uncovering works	19.3

Use before taking over	29.3

Valuation at Date of Termination	45.3

Variation Order Procedure	31.2

Vary, Engineer’s right to	31.1

War, etc., risk	44.1

Warranty for Patent Rights, Employer’s	16.3

Water, Gas and Electricity	14.3

Wayleaves, Consents, etc.	17.4

Working Hours	18.3

INDEX

Working Hours, Restriction of 	16.4

Workmanship	19.1

Work, resumption of 	24.4

Works, suspension of	23.1

Works, care of the	38.1

Works, damage after Risk Transfer Date	39.3

Works, damage before Risk Transfer Date	39.2

Works, insurance of	43.1

Works to be continued during arbitration	50.3

EDITORIAL AMENDMENTS

Following publication of the Third Edition of the Conditions of Contract for Electrical and Mechanical Works in 1987, a number of editorial amendments were agreed by FIDIC. The amendments have been incorporated during reprinting and the list below clarifies the differences between this copy and the original document.

Page 1	The following additional text has been inserted:

Commencement	Sub-Clause 1.1.1. (i)

date	The date for commencement of the Works is ___________________

Page 2	Sub-Clause 36.4(b) was previously Sub-Clause 36.4

The word ‘Sums’ following ‘shall be’ has been deleted.

Page 8	Sub-Clause 2.7. The missing letter ‘D’ has been inserted in ‘Disputing’ (margin note.)

Page 33	Sub-Clause 44.8(b). The word ‘Contractor’ on the last line was previously ‘Contract’.

Page 35	Sub-Clause 49.3. The word ‘or’ between ‘minute’ and ‘protocol’ was previously ‘of’.

Index, page (i)	The words ‘Adverse physical conditions and artificial obstructions’ have been deleted.

Index, page (v)	The word ‘adverse’ has been deleted after ‘Physical conditions’.

Contract Agreement 	The word ‘Agreement’ in the title has been capitalized.

Line 4	Inverted commas have been inserted after ‘Employer’.

Line 6	Inverted commas have been inserted before the word ‘the’ and deleted before the word ‘Contractor’.

Line 7	The comma following the word ‘executed’ has been deleted.

Line 15	Inverted commas have been inserted before the word ‘the’ and deleted after the word ‘the’.

Item 4, line 2	The word ‘defects’ was previously ‘defect’.

Item 4, line 3	The words ‘become’ was previously ‘become’.

Item 5, line 1	The words ‘and statutes or constitutions’ have been inserted after the word ‘laws’.

Item 5, line 2	The words ‘by their duly authorized signatories’ have been inserted after the word ‘hereof’.

Item 5	The remaining text of the original document has been deleted and is replaced by:

‘Binding Signatures(s) on behalf of the Employer _______________,

and

‘Binding Signatures(s) on behalf of the Contractor ______________,

PART-II: PARTICULAR CONDITIONS OF CONTRACT

(Mandatory Provisions- not to be amended / substituted except, where indicated by PEC)

PART-II: PARTICULAR CONDITIONS OF CONTRACT

1.1 Definitions

The text of Sub-Clause 1.1.1 is deleted and substituted by the following:

“Commencement Date” means the date specified in the Preamble to Conditions of Contract.

The text of Sub-Clause 1.1.2 is deleted and substituted by the following:

“Conditions” means the Preamble to Conditions of Contract, General Conditions of Contract and Particular Conditions of Contract.

Sub-Clause 1.1.3

At the end of Sub-Clause, the following is added:

“Any subsequent document mutually agreed and signed by the Employer and the Contractor, shall be the part of the Contract.”

The text of Sub-Clause 1.1.5 is deleted and substituted by the following:

“Contract Price” means the sum stated in the Letter of Acceptance as payable to the Contractor for the execution and completion of the Works subject to such additions thereto or deductions therefrom as may be made under the provisions hereinafter contained and remedying of any defects therein in accordance with the provisions of the Contract.”

Sub-Clause 1.1.11

The Defects Liability Period is the period mentioned in the Preamble to Conditions of Contract.

Sub-Clause 1.1.15

The following is added at the end of Sub-Clause:

“or any other competent person appointed by the Employer as his replacement.”

Sub-Clause 1.1.23

The following paragraph is added:

The word “Goods” is synonymous with “Plant.”

The text of Sub-Clause 1.1.27 is deleted and substituted by the following:

“Schedule of Prices” means the completed and priced Schedule of Prices, or any part or individual schedule thereof, submitted by the Contractor with his Bid or revised and mutually agreed and forming a part of the Contract documents.

Sub-Clause 1.1.33

The word “Tender” is synonymous with the word “Bid” and the word “Tender Documents” with the word “Bidding Documents”.

The following Sub-Clauses are added:

“1.1.38 “Month” means calendar month according to Gregorian calendar.

1.1.39	“Operation and Maintenance Manuals” has the meaning described in Sub-Clause 6.6.

Sub- Clause 1.1.40

“Warranty Certificate” means the certificate against specified goods/equipment, for the period mentioned in the Preamble to Conditions of Contract, to be issued by the Contractor that the goods/equipment supplied under the Contract are new, unused and incorporate all recent improvements in design and materials unless provided otherwise in the Contract and that the Contractor will be responsible for making good or replacing any defective goods/equipment during the Warranty Period specified in the Preamble to Conditions of Contract which should commence after expiry of Defect Liability Period.

Sub-Clause 1.1.41

The word “Part II” stated in FIDIC Conditions of Contract is synonymous with the word “Particular Conditions of Contract”.

Sub-Clause 1.6 Cost, Overhead Charges and Profit

The last sentence “Any profit ________ stated in the Preamble” is deleted and substituted by the following:

“Any profit entitlement shall be added to cost at the percentage stated in the Bid and agreed in the Contract Agreement.”

Sub-Clause 2.1 Engineer’s Duties

The text of Sub-Clause 2.1 is deleted and substituted by the following:

“The Engineer shall carry out the duties specified in the Contract.

The Engineer may exercise the authority attributable to the Engineer as specified in or necessarily to be implied from the Contract. The Engineer is required to obtain the specific approval of the Employer before carrying out his duties in accordance with the following Clauses of General Conditions of Contract:

(a)	approval of Subcontractor under Sub-Clause 4.1,

(b)	certifying additional sums under Sub-Clause 5.4,

(c)	certifying additional costs under Sub-Clauses 11.3 & 12.3,

(d)	certifying any cost under Sub-Clause 14.6,

(e)	approval of extension of time under Clause 26,

(f)	issuing a Taking–Over Certificate under Sub-Clause 29,

(g)	issuing a Defects Liability Certificate under Sub-Clause 30.11,

(h)	issuing a Variation Order under Clause 31,

(i)	fixing rates or prices under Clauses 31 and 34,

(j)	certifying additional costs under Sub-Clause 44.5 and

(k)	certifying additional costs under Sub-Clause 47.2;

Except for such variations pursuant to Sub-Clause 31.1 of the GCC which may be necessary in an emergency affecting safety of life, the works or of adjoining property.”

Except as expressly stated in the Contract the Engineer shall have no authority to relieve the Contractor of any of his obligations under this Contract.”

Sub-Clause 2.6 Confirmation in Writing

(i)	In line 3 after the words “undue delay” the following is added:	
“but not after the number of days mentioned in the Preamble to Conditions of Contract from the instruction or decision.”

(ii)	At the end of Sub-Clause 2.6, the following is added:

"The Engineer shall confirm or otherwise within the period mentioned in the Preamble to Conditions of Contract from the receipt of requirement(s) from the Contractor.”

Sub-Clause 2.7 Disputing Engineer’s Decisions and Instructions

The following text is deleted:

“If either party, ……………..in accordance with the Contract.”

Sub-Clause 2.8 Replacement of Engineer

The text of Sub-Clause 2.8 is deleted and substituted by the following:

“If the Employer intends to replace the Engineer, the Employer shall, not less than 14 days before the intended date of replacement, give notice to the Contractor, of the name, address and relevant experience of the intended replacement Engineer. The Employer shall not replace the Engineer with a person against whom the Contractor raises reasonable objection by notice to the Employer, with supporting particulars.”

Sub-Clause 2.9 Engineer Not Liable

Sub-Clause 2.9 is added as follows:

“Approval, reviews and inspection by the Engineer of any part of the Works does not relieve the Contractor from his sole responsibility and liability for the supply of remaining materials and equipment for the Works and parts thereof and complete the remaining erection works and testing and commissioning in accordance with the Contract and neither the Engineer's authority to act nor any decision made by him in good faith as provided for under this Contract whether to exercise or not to exercise such authority shall give rise to any duty or responsibility of the Engineer to the Contractor, any Subcontractor, any of their representatives or employees or any other person performing any of the works. However, the Contractor shall be compensated if any loss/damage is occurred due to the decision of the Engineer.”

Sub-Clause 4.2 No Contractual Relation between Subcontractor and the Employer

Sub-Clause 4.2 is added as follows:

Nothing contained in the Contract Documents shall create any contractual relation between any Subcontractor and the Employer.

Sub-Clause 5.3 Priority of Contract Documents

Sub-Clause 5.3 is deleted and substituted by the following:

“Unless otherwise provided in the Contract the priority of the Contract Documents shall be as follows:

1.	The Contract Agreement (if completed)

2.	The Letter of Acceptance

3.	The completed Form of Bid

4.	Preamble to Conditions of Contract

5.	The Particular Conditions of Contract

6.	The General Conditions of Contract

7.	The priced Schedule of Prices

8.	The completed Schedules to Bid

9.	The Specifications

10.	The Drawings

11.	 (Any other document)

In case of discrepancies between drawings, those of larger scale shall govern unless they are superseded by drawing(s) of a later date regardless of scale. All drawings and specifications shall be interpreted in conformity with the Contract Agreement and these conditions.”

Sub-Clause 5.4 Documents Mutually Explanatory

The text appearing in the last line after the words “the Contract Price” is deleted.

Sub-Clause 6.2 Consequences of Disapproval of Contractor's Drawings

Full stop is deleted and the following words are added at the end of Sub-Clause:

“for the approval of the Engineer. However, the Contractor shall not be entitled for time extension on this account.”

Sub-Clause 6.6. Operation and Maintenance Manuals

Paras 2&3 are deleted and the following text is added at the end of Para 1 of Sub-Clause:

“The Operation and Maintenance Manuals shall include full instructions for the operation, servicing and maintenance of the Plant, not only during the period of the Contractor's liability but more particularly during its operating life.

The directions shall be set out simply, clearly and systematically. This may be divided into two volumes if desirable, one for operation and the second for servicing and maintenance (in sub–volumes for major items of Plant).

The operational data shall include a complete physical and functional description of the Plant (in sub–volumes for major items of Plant) and step–by–step procedures for inspection, checking and adjustments for proper operation of the Plant.

The maintenance data shall include complete instructions for routine checks, servicing, maintenance and repair of all parts and for dismantling, handling and re–assembly of all equipment, sub–assemblies and all separate components. The maintenance data shall also include where possible parts catalogues. The lists shall provide all necessary information for identifying the parts and for re–ordering the parts including name of part, part number and catalogue references where applicable, name of manufacturer, size, capacity and other characteristics.

General arrangements, single line diagrams and detailed drawings shall be provided for ready reference in the operation and maintenance instructions.

The manuals shall be printed on ISO paper size A4 (210x297 mm) with offset or equivalent printing strongly bound in a durable stiff cover bearing the title in approved legend. Drawings shall be folded or reduced to 297 mm height. All volumes shall bear on the spine an approved shortened version of the title.

The Contractor shall submit three draft copies for approval of the Engineer prior to producing finished volumes.

The Contractor shall provide ten (10) copies of the approved Operation and Maintenance Manuals prior to Taking Over by the Employer. Supplementary Operation and Maintenance Manual shall be provided by the Contractor, if required, to incorporate changes resulting from experience during the operation and maintenance period. The work shall not be considered to be completed for the purpose of taking over until such manual and drawings have been supplied to the Employer.”

Sub-Clause 6.9 Manufacturing Drawings

The words “Unless otherwise specified in Part-II” are deleted and the following is added at the end of Sub-Clause:

“However, the Contractor is required to disclose to the Engineer or the Employer any confidential information necessary to justify the reliability, the efficiency and the operation and maintenance of the Plant supplied by him.”

Sub-Clause 6.10 “As–Built” Drawings

The following new Sub-Clause is added:

The Contractor shall furnish to the Engineer six (6) copies and one (1) reproducible of approved quality of all “As–Built” drawings within the period mentioned in the Preamble to Conditions of Contract.

Sub-Clause 8.1 General Obligations

The text of Sub-Clause 8.1 is deleted and substituted by the following:

“(a)	The Contractor shall commence the work on the date specified in the Preamble to Conditions of Contract and shall proceed with the same with due expedition and without delay.

(b)	The Contractor shall, in accordance with the Contract, with due care and diligence, complete the Works and test and commission the Plant and carry out the Works within the Time for Completion. The Contractor shall also provide all necessary Contractor's Equipment, superintendence, labour and except as stated hereinbelow, all necessary facilities therefor.

The Employer will permit use of the Erection, Testing Equipment and Maintenance Tools as stated in the Preamble to Conditions of Contract.

The above facilities shall be provided at no cost to the Contractor but he shall procure at his cost all required consumable materials and any other items necessary for the proper execution of the Works. These shall be properly used and maintained by the Contractor and returned to the Employer upon handing over of the Works in good condition, fair wear and tear excepted. In case of any damage, loss or theft, the items shall be replaced by the Contractor at his own cost.”

Sub-Clause 10.1 Performance Security

Sub-Clause 10.1 is deleted and substituted by the following:

“The Contractor shall provide a Performance Security in the prescribed Form annexed to these Documents. The said Security shall be furnished by the Contractor within 28 days after the receipt of Letter of Acceptance. The Performance Security shall be of an amount equal to 10 percent of the Contract Price in the currency of the Contract at the option of the bidder, in the form of Bank Guarantee from any Scheduled Bank in Pakistan or from a bank located outside Pakistan duly counter-guaranteed by a Scheduled Bank in Pakistan.

The cost of complying with the requirements of this Sub-Clause shall be borne by the Contractor.”

Sub-Clause 10.3 Claims under Performance Security

Sub-Clause 10.3 is deleted in its entirety.

The following Sub Clause is added:

Sub-Clause 10.4 Performance Security Binding on Variations and Changes

“The Performance Security shall be binding irrespective of variations and changes in the quantities of the Works or extensions in completion time of the Works, which are granted or agreed upon under the provisions of the Contract.”

Sub-Clause 12.1 Programme to be Furnished

Sub-Clause 12.1(a) is deleted and substituted by the following:

“(a)	the order in which the Contractor proposes to carry out the Works (including preliminaries, required material ordering, delivery to Site, erection and rectifications work, testing, commissioning and taking–over by the Employer). The programme shall also include the following:

(i)	Employment of local and expatriate Labour of various categories,

(ii)	Local material procurement,

(iii)	Material imports, if any.”

In Sub-Clause 12.1(c)(iv) the words “any import licenses” are deleted.

Sub-Clause 12.4 Monthly Progress Report

The following Sub-Clause 12.4 is added:

“During the period of the Contract, the Contractor shall submit six sets of report to the Engineer not later than the 8th day of each month, including:

(i)	a construction schedule indicating the progress achieved during the preceding month;

(ii)	description of all work carried out since the last report;

(iii)	description of the work planned for the next forty-two days sufficiently detailed to enable the Engineer to determine his programme of inspection and testing;

(iv)	summary of daily job record for the preceding month; and

(v)	colour photographs to illustrate progress.

Sub-Clause 12.5 Daily Job Record

The following Sub Clause 12.5 is added:

“During the period of the Contract, the Contractor shall keep a daily record of the work progress, which shall be made available to the Engineer as and when requested.

The daily record shall include particulars of weather conditions, number of men working, in different categories, deliveries of materials, quantity, location and assignment of equipment.”

Sub-Clause 13.1 Contractor's Representative

At the end of the Sub-Clause the following is added:

“The Contractor's Representative shall be a competent and skilled person approved by the Engineer (which approval may at any time be withdrawn) and who shall be present on the Site during all working hours. He shall be fluent in the English language. He shall not be transferred from the Site without the consent of the Engineer.

Sub-Clause 13.3 Language Ability of Superintending Staff of Contractor

The following Sub-Clause 13.3 is added:

“A reasonable proportion of the Contractor's superintending staff shall have a working knowledge of the English language.”

Sub-Clause 14.1 Contractor's Equipment

Replace the word “or” at the end of Sub-paragraph (a) by the word “and” and insert the following at the end of Sub-paragraph(b):

“which shall not be unreasonably withheld.”

Sub-Clause 14.2 Safety Precautions

At the end of the Sub-Clause the following is added:

“In order to provide for the safety, health and welfare of persons, and for prevention of damage of any kind, all operations for the purposes of or in connection with the Contract shall be carried out in compliance with the safety requirements of the Government of Pakistan with such modifications thereto as the Engineer may authorise or direct and the Contractor shall take or cause to be taken such further measures and comply with such further requirements as the Engineer may determine to be reasonably necessary for such purpose.

The Contractor shall make, maintain, and submit reports to the Engineer concerning safety, health and welfare of persons and damage to property as the Engineer may from time to time prescribe.”

Sub-Clause 14.3 Electricity Water and Gas

The text of Sub-Clause 14.3 is deleted and substituted by the following:

“The Contractor shall be responsible for making his own arrangements for the adequate supply of electricity, water and gas required for the effective performance of his obligations under the Contract. Subject to the aforesaid, the Contractor shall be entitled to use for the purposes of the Works such supplies and services as may be available on the Site. The Contractor shall, before the commencement of the work at Site, seek the approval of the Engineer as to his detailed requirements of electricity, water and gas for the entire Contract period. The Contractor shall pay the Employer at the rates/cost incurred by the Employer. The Contractor shall at his own cost provide any apparatus necessary for such use.”

Sub-Clause 14.4 Employer’s Equipment

The text of Sub-Clause 14.4 is deleted and substituted by the following:

“The Employer shall, if the Contractor so requests for the execution of the works, operate any available equipment of which details are given in the Preamble to Conditions of Contract. The Contractor shall pay the Employer a mutually agreed price for such use.

The Employer shall during such operation retain control of and be responsible for the safe working of the equipment.

Sub-Clause 14.8 Information for Import Permits & Licenses

The text of Sub-Clause 14.8 is deleted and substituted by the following:

“The Contractor shall submit to the Employer in good time such details of all Plant and Contractor's Equipment as is to be imported into Pakistan and identify as to what assistance of the Employer is required for obtaining by the Contractor of all necessary import permits or licenses.”

Sub-Clause 15.2 Compliance with Laws

The Sub-Clause 15.2 is deleted and substituted by the following:

“The Contractor shall comply with the Laws of country of manufacture and the Laws of Pakistan where the Plant is to be erected.”

Sub-Clause 16.4 Photographs of Works and Advertisement Prohibited

Sub-Clause 16.4 is added:

“Except with the prior written authorization of the Employer the Contractor shall not exhibit or permit to be exhibited any photographs or advertisement on the Works. Any authorized exhibition shall be immediately removed if the Employer so requires.”

Sub-Clause 16.5 Training of Employer's Staff

Sub-Clause 16.5 is added:

“The Contractor shall provide such facilities for the training of such numbers of Pakistani engineers, engineering students, apprentices and trade apprentices on such sections of the Works at the Site or on the Contractor’s premises or Contractor selected plant manufacturer's premises and factories, or wherever else work is in hand, as specified or directed by the Engineer. The Employer shall direct what sums by way of wages and allowances are to be paid by the Contractor to such persons and shall reimburse the Contractor for such sums as are so directed to be paid and are paid. The Contractor shall also provide medical expenses or medical insurance and travelling expenses for trainees if required by the Employer which shall be reimbursed by the Employer.

The language of training at the above stated premises shall be English.”

Sub-Clause 17.4 Consents and Way Leaves

The Sub-Clause 17.4 is deleted and substituted by the following:

The Employer shall issue permissions, letters, certificates and provide such other assistance to the Contractor for his obtaining permits-to-work, way leaves and approvals from any other department/authority and right of way from private owners, if required. The Contractor will bear the cost of logistics, fees, etc. for such activities. The Employer, will reimburse the Contractor only the payments made by him in respect of any land compensation for obtaining such way leaves, required for the Works.

Sub-Clause 17.5 – Import Permits and Licenses

The word “Employer” is deleted and substituted by the word “Contractor” and the following is added at the end of Sub-Clause 17.5:

“the Employer will provide assistance for this purpose.”

Sub-Clause 18.1 – Engagement of Labor

At the end of the Clause the following is added:

“in accordance with the regulations, orders and requirements of the Govt. of Pakistan.”

Sub-Clauses 18.5 to 18.12 are added:

“Sub-Clause 18.5 Employment of Persons in the Service of Others

The Contractor shall not recruit or attempt to recruit staff and labor from amongst the persons in the service of the Employer or the Engineer and vice–versa, unless mutually agreed between the Employer/Engineer and the Contractor

Sub-Clause 18.6 Alcoholic Liquor or Drugs

The Contractor shall not, otherwise than in accordance with the Statutes, Ordinances and Government Regulations or Orders for the time being in force, import, sell, give, barter or otherwise dispose of any alcoholic liquor or drugs, or permit or suffer any such importation, sale, gift, barter or disposal by his Subcontractors, agents, employees or Labour.

Sub-Clause 18.7 Arms and Ammunition

The Contractor shall not give, barter or otherwise dispose of to any person or persons, any arms or ammunition of any kind or permit or suffer the same as aforesaid.

Sub-Clause 18.8 Festivals and Religious Customs

The Contractor shall in all dealings with his staff and labor have due regard to all recognized festivals, days of rest and religious or other customs.

Sub-Clause 18.9 Disorderly Conduct

The Contractor shall at all times take all reasonable precautions to prevent any unlawful riotous or disorderly conduct by or amongst his staff and labor and for the preservation of peace and protection of persons and property in the neighborhood of the Works.

Sub-Clause 18.10 Records of Safety and He

The Contractor shall maintain such records and make such reports concerning safety, health and welfare of persons and damage to property as the Engineer may from time to time prescribe.

Sub-Clause 18.11 Reporting of Accidents

The Contractor shall report to the Engineer details of any accident as soon as possible after its occurrence. In the case of any fatality or serious accident, the Contractor shall, in addition to appropriate action required under the law, notify the Engineer immediately by the quickest available means.

Sub-Clause 18.12 Compliance by Subcontractors

The Contractor shall be responsible for compliance by his Subcontractors of the foregoing provisions.”

Sub-Clause 19.1 Manner of Execution

The following is added at the end of Sub-Clause:

“The Contractor shall submit for approval of the Engineer, his detailed method statement(s) for the execution of such items of work as may be desired by the Engineer. Approval of such method statement(s) shall neither relieve the Contractor of his responsibilities under the Contract nor form any basis for claiming additional costs.”

Sub-Clause 19.3 Uncovering Work

The following is added at the end of second paragraph of Sub-Clause 19.3:

“In any other case, all costs shall be borne by the Contractor.”

Sub-Clause 19.4 Use of Pakistani Materials

The following Sub-Clause 19.4 is added:

“The Contractor shall so far as may be consistent with the Contract make the maximum use of materials, supplies and equipment indigenous to or produced in Pakistan and services available in Pakistan or operated in Pakistan provided such materials, supplies, equipment and services shall be of required standard.”

Sub-Clause 24.1 Cost of Suspension

At the end of the second paragraph after the word “Contractor” the following is added:

“or for the proper execution or for the safety of the Works or Plant unless such necessity results from any act or default of the Engineer or the Employer or in consequence of any of the Employer's Risks under Sub-Clause 37.2.”

Sub-Clause 24.4 Resumption of Work

First paragraph of Sub-Clause 24.4 is deleted and substituted by the following:

“If the Contractor chooses not to treat prolonged suspension as an omission or termination under Sub-Clause 24.3, the Employer shall, upon the request of the Contractor, take over the responsibility for protection, storage, security and insurance of the suspended Works and of the Plant which has been delivered to the Site and which is affected by suspension and the risk of loss or damage thereto shall thereupon pass to the Employer.”

Sub-Clause 25.1 Time for Completion

The text of Sub-Clause 25.1 is deleted and substituted by the following:

“The Delivered Plant at the place of the project mentioned in the Preamble to Conditions of Contract shall be completed tested and commissioned within the period mentioned in the Preamble to Conditions of Contract.”

Sub-Clause 26.1 Extension of Time for Completion

Sub-Clause 26.1(h) is deleted.

Sub-Clause 26.3 Earlier Completion

(i)	At the end of Sub-Clause 26.3(a) the following text is added and Clause is re-designated as 26.3.

“The extra sum to be paid to the Contractor for Completion of Works prior to the date of Completion established under Sub-Clause 25.1 shall be computed on the basis of the sums mentioned in the Preamble to Conditions of Contract.”

(ii)	Sub-Clause 26.3 (b) is deleted.

“Sub-Clause 26.4 Rate of Progress

Sub-Clause 26.4 is added:

“If for any reason, which does not entitle the Contractor to an extension of time, the rate of progress of the Works or any Section is at any time, in the opinion of the Engineer, too slow to comply with the Time for Completion, the Engineer shall so notify the Contractor who shall thereupon take such steps as are necessary, subject to the consent of the Engineer, to expedite progress so as to comply with the Time for Completion. The Contractor shall not be entitled to any additional payment for taking such steps. If, as a result of any notice given by the Engineer under this Clause, the Contractor considers that it is necessary to do any work at night or on locally recognized days of rest, he shall be entitled to seek the consent of the Engineer so to do. Provided that if any steps, taken by the Contractor in meeting his obligations under this Sub-Clause, involve the Employer in additional supervision costs, such costs shall, after due consultation with the Employer and the Contractor, be determined by the Engineer and shall be recoverable from the Contractor by the Employer, and may be deducted by the Employer from any moneys due or to become due to the Contractor and the Engineer shall notify the Contractor accordingly, with a copy to the Employer.”

Sub-Clause 27.1 Delay in Completion

Sub-Clause 27.1 is deleted and substituted by the following:

“If the Contractor fails to deliver the Plant, or any part thereof, within the time stated in Sub-Clause 25.1, or fails to complete the whole of the Goods, or, if applicable, any Section within the relevant time prescribed by Sub-Clause 25.1, then the Contractor shall pay to the Employer the relevant sum stated herein below as liquidated damages for such default (which sum shall be the only moneys due from the Contractor for such default) for every day or part of a day which shall elapse between the relevant time for Delivery or Time for Completion and the actual date of delivery at site or the date stated in a Taking–Over Certificate of the whole of the Goods or the relevant Section, as the case may be, subject to the applicable limit stated herein below.

The Employer may deduct the amount of such damages from any monies due or to become due to the Contractor. The payment or deduction of such damages shall not relieve the Contractor from his obligation to complete the Delivery of Goods, or from any other of his obligations & liabilities under the Contract.”

The liquidated damages for each day of delay and the maximum amount of liquidated damages shall be the amounts mentioned in the Preamble to Conditions of Contract.

Sub-Clause 28.7 Consequences of Failure to Pass Tests on Completion

The words “by arbitration” appearing at the end of the Sub-Clause 28.7(c) are deleted and substituted by the words “by the Engineer”.

Sub-Clause 30.4 Extension of Defects Liability Period

At the end of 4th paragraph of Sub-Clause the following is added:

“or a mutually agreed period.”

Sub-Clause 30.5 Failure to Remedy Defects

In first line after the words “reasonable time” the following is added:

“fixed by the Engineer”.

Sub-Clause 30.13 Unfulfilled Obligations

New Sub-Clause 30.13 is added as herein below:

“After the Defects Liability Certificate has been issued, the Contractor and the Employer shall remain liable for the fulfillment of any obligation which remains unperformed at that time. For the purposes of determining the nature and extent of any such obligation, the Contract shall be deemed to remain in force.”

Sub-Clause 31.1 Engineer's Right to Vary

The following is added at the end of second paragraph:

“No such variation shall in any way vitiate or invalidate the Contract, but the effect, if any, of all such variations shall be valued in accordance with Clause 31. Provided that where the issue of an instruction to vary the Works is necessitated by some default of or breach of Contract by the Contractor or for which he is responsible, any additional cost attributable to such default shall be borne by the Contractor.”

Sub-Clause 31.5 Record of Costs

The word “Engineer” in 4th line of Sub-Clause is deleted and substituted by “Engineer/Employer”.

Sub-Clause 31.6 Day work under Variation Order

New Sub-Clause 31.6 is added as given below:

“A Variation Order may provide that work done pursuant thereto shall be executed as Day work. In such case the Contractor shall be paid for such work under the conditions and the rates and prices set out in the Day Work Schedule.”

Sub-Clause 31.7 Value Engineering

New Sub-Clause 31.7 is added as given below:

The Contractor may, at any time, submit to the Engineer a written proposal which in the Contractor’s opinion will reduce the cost of constructing, maintaining or operating the works, or improve the efficiency or value to the Employer of the completed Works or otherwise be of benefit to the Employer. Any such proposal shall be prepared at the cost of the Contractor. However, Employer is not bound to accept such proposal.

Sub-Clause 33.1 Terms of Payment

PAYMENT ON PRORATA BASIS (On individual project basis) Imported Items

- Submission of Detailed Technical Specifications, Drawings, Powerhouse Foundation Drawings and Design along with Workplan on time scale basis by the contractor and approval by the Employer for the project and submission of performance bond AA rated insurance company or against irrevocable bank guarantee on the prescribed form in the name of AKRSP for the contract period from a scheduled bank of Pakistan of PO value. 25%

- Opening of Letter of Credit (LC) provide proof of payment to vendor and provision of confirmation document to the Employer. 25%

- Pre-Delivery Inspection/FAT/quality checking and Shipment clearance at port. 20%

- Complete Transportation safely to the MHP site. 10%

- On site Installation, Testing and Commissioning 15%

- Defect Liability Period (365 days) 5%

Sub-Clause 33.1.1 Retention of Payment

If at any time any payment would fall due for Goods or part of Goods and, if there shall be any defect in part of such Goods in respect of which such payment is proposed, the Employer may retain the whole or any part of such payment. Any sum retained by the Employer pursuant to the provisions of this Clause shall be paid to the Contractor after the said defect is removed.

Sub-Clause 33.2 Method of Application

(Employer may vary this Sub-Clause)

Sub-Clause 33.5 Payment

Sub-Clause 33.5 is deleted and substituted by the following:

The amount due to the Contractor under any Interim Payment Certificate issued by the Engineer pursuant to this Clause, or to any other term of the Contract, shall, subject to Clause 27, be paid by the Employer to the Contractor within 30 days after such Interim Payment Certificate has been jointly verified by Employer and Contractor, or, in the case of the Final Certificate referred to in Sub-Clause 33.10 within 60 days after such Final Payment Certificate has been jointly verified by Employer and Contractor; Provided that the Interim Payment shall be caused in 42 days and Final Payment in 60 days in case of foreign funded project.

Deduction shall be made from the net amounts payable to the Contractor of any sum(s) in accordance with the prevalent Federal and/or Provincial laws, provided that no such deduction shall be made from those payments in respect of which the Contractor has obtained exemption under the Law.”

Sub-Clause 33.6 Delayed Payment

The Payment will be made subject to the release of fund

Sub-Clause 33.8 Payment by Measurement

The work shall be measured for the units mentioned in the Schedule of Prices according to the Contract as determined by the Engineer from approved drawings, Specifications and Contract Documents.

Sub-Clause 33.12 Withholding of Payment

New Sub-Clause 33.12 is added as given below:

If the Goods or any part thereof is not being carried out to the Engineer's satisfaction and in order to protect the Employer from loss on account of:

(a)	defective work not rectified

(b)	guarantees not met

(c)	claims filed against the Contractor

(d)	failure of the Contractor to make payments due for Plant procured or labour employed by him.

(e)	damage to any other contractor employed by the Employer.

(f)	Contractor's non–compliance with the Contract

(g)	any Government dues recoverable from the Contractor if notified by the Government

The Engineer may notify withholding of such payments or part thereof as may, in his opinion, be related to the aforesaid reasons/grounds. When the reasons/grounds for withholding the payment are removed by the Contractor, the Engineer shall upon being satisfied to that effect issue Certificate of Payment in respect of withheld amounts.

Sub-Clause 35.1 Payment in Foreign Currencies

(Employer may vary this Sub-Clause)

Sub-Clause 35.2 Currency Restrictions

The text of Sub-Clause 35.2 is deleted and substituted by the following:

“Any required foreign currency transactions shall be met by the Employer/Contractor at his cost from his own resources.”

Sub-Clause 35.3 Rates of Exchange

The words “as stated in the Preamble” appearing in 3rd line of Sub-Clause are deleted and substituted by the words “as published or authorized by State Bank of Pakistan”.

Sub-Clause 36.4 Payment against Provisional Sums

Sub-Clause 36.4 is deleted and substituted by the following:

“Provisional Sum if any will be expended on the direction of the Engineer through Variation Orders which would be valued in accordance with the provisions of Clause 31 Conditions of Contract.”

Sub-Clause 37.2 Employer's Risks

The text of Sub-Clause 37.2 is deleted and substituted by the following:

“The Employer's Risks are:

(a)	(Insofar as they relate to Pakistan) war and hostilities (whether war be declared or not), invasion, act of foreign enemies

(b)	(Insofar as they relate to Pakistan) rebellion, revolution, insurrection, military or usurped power or civil war

(c)	ionizing radiation or contamination by radioactivity from any nuclear fuel, radio-active toxic explosives or other hazardous properties of any explosive nuclear assembly or nuclear components thereof

(d)	pressure waves caused by aircraft travelling at sonic or supersonic speed

(e)	(Insofar as they relate to Pakistan) riot, commotion or disorder, unless solely restricted to the employees of the Contractor or of his Subcontractors

(f)	use or occupation of the Work or any part thereof by the Employer

(g)	fault, error, defect or omission in the design of any part of the Works by the Engineer, Employer or those for whom the Employer is responsible for which the Contractor has disclaimed responsibility in writing within a reasonable time after the receipt of such design

(h)	the use or occupation of the Site by the Works or any part thereof, or for the purposes of the Contract: or interference, whether temporary or permanent with any right of way, light, air or water or with any easement, way leaves or right of a similar nature which is the inevitable result of the construction of the Works in accordance with the Contract

(i)	the right of the Employer to construct the Works or any part thereof on, over, under, in or through any land

(j)	damage (other than that resulting from the Contractor's method of construction) which is the inevitable result of the construction of the Works in accordance with the Contract

(k)	the act, neglect or omission or breach of contract or of statutory duty of the Engineer, the Employer or other contractors engaged by the Employer or of their respective employees or agents.”

Sub-Clause 39.2 Loss or Damage Before Risk Transfer Date

The words “by arbitration under Clause 50” are deleted and substituted by the words “by the Engineer”.

Sub-Clause 39.4 Duty to Minimize Delay

New Sub-Clause 39.4 is added as given below:

Each Party shall at all times use all reasonable endeavours to minimize any delay in the Performance of the Contract as a result of Risks.

The Contractor shall give notice to the Employer and vice versa the Employer shall give notice to the Contractor in case of foreseeable delay by the Risks.

Sub-Clause 40.2 Employer's Liability

The text of Sub-Clause 40.2 from the words “or of death or personal injury” to the end of the Sub-Clause, is deleted and substituted by the following:

“........ (other than the Works) or of death or personal injury to the extent caused by any of the Employer's Risks listed in paragraphs (f), (g), (h), (i), (j), and (k) of Sub-Clause 37.2 but not otherwise.”

Sub-Clause 42.2 Maximum Liability

the words “the sum stated in the Preamble to Conditions of Contract or if no such sum is stated” appearing in 2nd line of Sub-Clause is deleted.

Sub-Clause 42.6 Foreseen Damage

Sub-Clause 42.6 is deleted in its entirety.

Sub-Clause 43.1 The Works (Insurance)

(Employer may vary this Sub-Clause)

Sub-Clause 43.2 Contractor's Equipment

Sub-Clause 43.2 is deleted and substituted by the following:

“The Contractor shall insure the Contractor's Equipment for its full replacement value while on the Site against all loss or damage caused by any of the Contractor's Risks.”

Sub-Clause 43.3 Third Party Liability (Insurance)

(Employer may vary this Sub-Clause)

Sub-Clause 43.7 Remedies on the Contractor’s Failure to Insure

In 3rd line after the word, “purpose”, the expressions- “and reasonable costs including the man-hours costs of Employer’s Personnel” are added.

Sub-Clause 43.9 Currency of Insurance

New Sub-Clause 43.9 is added as given below:

“All policies of Insurance of the Plant shall provide for payment of indemnity to be made in such amounts as will allow making good of loss of or damage to the whole or any part of the Goods.”

Sub-Clause 43.10 Contractor to Notify

New Sub-Clause 43.10 is added as given below:

“It shall be the responsibility of the Contractor to notify the insurance company of any changes in nature and extent of the Goods and to ensure the adequacy of the insurance coverage at all times in accordance with the provisions of the Contract.”

Sub-Clause 43.11 Procurement of Insurance Policies

New Sub-Clause 43.11 is added as given below:

“The Contractor shall procure and submit the insurance cover under this Clause within a period of 28 days from the date of receipt of Letter of Acceptance from the Employer.”

Sub-Clause 44.6 Damage Caused by Force Majeure

At the end of the Sub-Clause 44.6 the following is added:

“However, the Contractor shall put up his claim to the Employer / Engineer with full details and justification.”

Sub-Clause 44.8 Payment on Termination for Force Majeure

Text in sub-para (c) is deleted and para (d) and (e) are re-numbered as (c) and (d).

Sub-Clause 44.10 Force Majeure Affecting Engineer’s Duties

Sub-Clause 44.10 is deleted in its entirety.

Sub-Clause 45.2 Contractor's Default

The following paragraph is added at the end of Sub-Clause 45.2.

“The Employer or such other contractor may use for such completion any Contractor's Equipment which is upon the Site as he or they may think proper, and the Employer shall pay the Contractor a reasonable compensation for such use”.

Sub-Clause 45.6 is added as follows:

Sub-Clause 45.6 Integrity Pact

If the Contractor, or any of his Subcontractors, agents or servants is found to have violated or involved in violation of the Integrity Pact signed by the Contractor as Schedule-H to his Bid, then the Employer shall be entitled to:

- recover from the Contractor an amount equivalent to ten times the sum of any commission, gratification, bribe, finder’s fee or kickback given by the Contractor or any of his Subcontractors, agents or servants;

- terminate the Contract; and

- recover from the Contractor any loss or damage to the Employer as a result of such termination or of any other corrupt business practices of the Contractor or any of his Subcontractors, agents or servants.

The termination under Sub-Para (b) of this Sub-Clause shall proceed in the manner prescribed under Sub-Clauses 45.2 to 45.5 and the payment under Sub-Clause 45.4 shall be made after having deducted the amounts due to the Employer under Sub-Para (a) and (c) of this Sub-Clause.

Sub-Clause 46.1 Employer's Default

The comma and the word “or” at the end of paragraph (d) of Sub-Clause 46.1 are deleted and substituted by period (.) Paragraph (e) of Sub-Clause 46.1 is deleted.

Sub-Clause 46.3 Payment on Termination for Employer's Default

The words “including loss of profit” in the second paragraph of Sub-Clause 46.3 are deleted.

Sub-Clause 47.1 Labour, Materials and Transport

(Employer to modify this Sub-Clause as provided under Clause 70.1 of PCC of PEC Civil Documents and following PEC Procedure and Formula for Price Adjustment)

Sub-Clause 48.1 Customs and Import Duties

(Employer may vary this Sub-Clause)

The Sub-Clause 48.3 is added:

Sub-Clause 48.3 Port Charges and Port Congestion

The Contractor shall be deemed to have obtained all the information regarding facilities and charges, in respect of port clearance, loading and unloading, storage, transportation, congestion and confirmed the requirements thereof at his own responsibility and all such costs and charges are deemed to be included in the rates and prices of the Schedule of Prices.

Sub-Clause 49.1 Notice to Contractor

The following is added at the end of Sub-Clause 49.1:

“For the purposes of Sub-Clause 49.1 the Contractor shall, immediately after receipt of Letter of Acceptance, intimate in writing to the Employer and the Engineer by registered post, the address of his principal place of business or any change in such address during the period of the Contract.”

Sub-Clause 50 Disputes & Arbitration

Clause 50 is deleted and in its place the following Sub-Clauses 50.1 to 50.5 are inserted:

“50.1	If a dispute of any kind whatsoever arises between the Employer and the Contractor in connection with, or arising out of, the Contract or the execution of the Works, whether during the execution of the Works or after their completion and whether before or after repudiation or other termination of the Contract, including any dispute as to any opinion, instruction, determination, certificate or valuation of the Engineer, the matter in dispute shall, in the first place, be referred in writing to the Engineer, with a copy to the other party. Such reference shall state that it is made pursuant to this Clause. No later than the fifty sixth (56) day after the day on which he received such reference, the Engineer shall give notice of his decision to the Employer and the Contractor. Such decision shall state that it is made pursuant to this Clause.

Unless the Contract has already been repudiated or terminated, the Contractor shall, in every case, continue to proceed with the Work with all due diligence, and the Contractor and the Employer shall give effect forthwith to every such decision of the Engineer unless and until the same shall be revised, as hereinafter provided in an amicable settlement or in an arbitral award.

In any case where the Conditions of Contract provide that the decision of the Engineer is to be final and conclusive, such decision shall not be referable to arbitration under this Clause nor shall the same be questioned in any other form of proceedings whatsoever.

50.2	If either the Employer or the Contractor be dissatisfied with a decision of the Engineer or if the Engineer fails to give notice of his decision on or before the fifty sixth (56) day after the day on which he received the reference, then either the Employer or the Contractor may, on or before the twenty eighth (28) day after the day on which the said period of fifty six (56) days expired, as the case may be, give notice to the other party to commence arbitration, as hereinafter provided, as to the matter in dispute. Such notice shall establish the entitlement of the party giving the same to commence arbitration, as hereinafter provided, as to such dispute and, subject to Sub-Clause 50.5, no arbitration in respect thereof may be commenced unless such notice is given.

If the Engineer has given notice of his decision as to a matter in dispute to the Employer and the Contractor and no notification of intention to commence arbitration as to such dispute has been given by either the Employer or the Contractor on or before the twenty eighth (28) day after the day on which the parties received notice as to such decision from the Engineer the said decision shall become final and binding upon the Employer and the Contractor.

50.3	Where notice of intention to commence arbitration as to a dispute has been given in accordance with Sub-Clause 50.2, arbitration of such dispute shall not be commenced unless an attempt has first been made by the parties to settle such dispute amicably through mutual negotiation within ninety (90) days from the date of notification of Engineer’s decision.

50.4	Any dispute in respect of which:

(a)	the decision, if any, of the Engineer has not become final and binding pursuant to Sub-Clause 50.1 and

(b)	amicable settlement has not been started/reached within the period stated in Sub-Clause 50.3

shall be finally settled, unless otherwise specified in the Contract, under the Pakistan Arbitration Act, 1940 (Act No. X of 1940) and Rules made there under as amended, by one or more arbitrators appointed under such Rules.

The said arbitrator(s) shall have full power to open up, review and revise any decision, opinion, instruction, determination, certificate or valuation of the Engineer for the purpose of obtaining said decision pursuant to Sub-Clause 50.1. No such decision shall disqualify the Engineer from being called as a witness and giving evidence before the arbitrator(s) on any matter whatsoever relevant to the dispute.

The venue of arbitration proceedings shall be the place in Pakistan as mentioned in the Preamble to Conditions of Contract.

50.5	Where neither the Employer nor the Contractor has given notice of intention to commence arbitration of a dispute within the period stated in Sub-Clause 50.1 or 50.2 and the related decision has become final and binding, either party may, if the other party fails to comply with such decision, and without prejudice to any other rights it may have, refer the failure to arbitration in accordance with Sub-Clause 50.4. The provisions of Sub-Clauses 50.1 to 50.2 shall not apply to any such reference.”

Other terms & conditions:

- The contract shall submit irrevocable performance guarantee equal to 10% of the contract price for the contract period from a reputable international bank or from an insurance company having +AA rating in the name of AKRSP within 14 days after issuance of acceptance letter. The bid security will be release on production of performance guarantee. In case of no submission of the said guarantee the bid security shall be forfeited and the bid shall be rejected. The performance guarantee shall be release after successful commissioning of the Hydrogenator sets and on expiry of defect liability period.

- The income tax at the rates fixed by the government of Pakistan shall be deducted from each bill.

- All the payments to the contractor shall be made in PKR.

Other terms & conditions:

- The contractor shall submit the technical and financial proposals and bid security sealed in separate envelops and all sealed in one envelope.

- Evaluation shall be done separately and awarded to the most advantageous evaluated bidder.

- AKRSP is the employer, however tenders shall be opened and evaluated through a committee of officers constituted by the competent authority.

- The bidder shall quote his rates in the financial bid in PKR.

- The bidder should quote rate for all the scope of work and each item separately to facilitate evaluation of the bid.

- The duties, taxes, fees etc. should be entered in the schedule of the price according to the present SRO’s of the government and in case of changes in the government legislation the same shall be paid/deducted on the basis of actual invoices submitted by the contractor. No price escalation shall be paid to the contractor for increase in the prices of the materials used for manufacturing of the equipment included in the contract and their transportation, installation/commissioning.

- The Employer is empowered to reject any or all bids without assigning any reason.

- The bidder shall submit test certificate of chemicals composition and mechanical properties of metals being used for manufacturing of the turbo generators.

- All equipment should be tested prior to delivery/shipment at manufacturers premises and test certificates shall submit.

- The quality of all machinery, equipment, auxiliaries, wiring etc. should conform to the international standard mentioned in the section specification/special provisions.

- The place of the delivery of each turbo generator is the installation site of the project.

- The specification given in the documents are minimum and for the guidance of the contractor/manufacturer. The designer/manufacturer is at liberty and welcome to adopt better specification.

- The defect liability period of the turbo generators and auxiliaries will be 12 months after commissioning and test running of the units. The contractor shall be liable to repair and make good free of charge any defects in design, materials, workmanship and error in installation that may arise to the product supplied by him. The cost of the replacement of defective parts and components shall be borne by the contractor.

- The bidder shall submit a certificate from the manufacturer guaranteeing the efficiencies of the turbine and generator offered in the technical proposal/bidding document.

- During final testing of the turbo generator at site, if the overall efficiency of the plant is found lesser than the guaranteed efficiency of the bid, recovery shall be made from the contractor at the price adjustment rate for each unit for 0.1% reduction in efficiency given in clause IB 26.3. However, no payment shall be made for higher efficiencies.

STANDARD FORMS

STANDARD FORMS

Page No.

Standard Forms include the following:

- Form of Bid Security	152

(Bank Guarantee)

- Form of Contract Agreement	154

- Form of Performance Security

(Bank Guarantee)	156

- Form of Bank Guarantee/Bond for Advance Payment	158

(Note: Standard Forms provided in this document for securities are to be issued by a bank. In case the bidder chooses to issue a bond for accompanying his bid or performance of contract or receipt of advance, the relevant format shall be tailored accordingly without changing the spirit of the Forms of securities).

FORM OF BID SECURITY

(Bank Guarantee)

Guarantee No._____________________

Executed on _____________________

Expiry date _____________________

[Letter by the Guarantor to the Employer]

Name of Guarantor (Bank) with address:_______________________________________

Name of Principal (Bidder) with address:_____________________________________

________________________________________________________________________

Penal Sum of Security (express in words and figures):_____________________________

________________________________________________________________________

Bid Reference No.___________________________ Date of Bid ______________

KNOW ALL MEN BY THESE PRESENTS, that in pursuance of the terms of the Bid and at the request of the said Principal, we the Guarantor above-named are held and firmly bound unto the __________________________________, (hereinafter called The “Employer”) in the sum stated above, for the payment of which sum well and truly to be made, we bind ourselves, our heirs, executors, administrators and successors, jointly and severally, firmly by these presents.

THE CONDITION OF THIS OBLIGATION IS SUCH, that whereas the Principal has submitted the accompanying Bid numbered and dated as above for ________________________________________ (Particulars of Bid) to the said Employer; and

WHEREAS, the Employer has required as a condition for considering the said Bid that the Principal furnishes a Bid Security in the above said sum to the Employer, conditioned as under:

(1)	that the Bid Security shall remain valid for a period 28 days beyond the period of validity of the Bid;

(2)	that in the event of;

(a)	the Principal withdraws his Bid during the period of validity of Bid, or

(b)	the Principal does not accept the correction of his Bid Price, pursuant to Sub-Clause 24.2 of Instructions to Bidders, or

(c)	failure of the successful bidder to

(i)	furnish the required Performance Security, in accordance with Clause 34 of Instructions to Bidders, or

(ii)	sign the proposed Contract Agreement, in accordance with Clause 35 of Instructions to Bidders,

then the entire sum be paid immediately to the said Employer as liquidated damages and not as penalty for the successful bidder's failure to perform.

NOW THEREFORE, if the successful bidder shall, within the period specified therefor, on the prescribed form presented to him for signature enter into a formal Contract with the said Employer in accordance with his Bid as accepted and furnish within twenty eight (28) days of his being requested to do so, a Performance Security with good and sufficient surety , as may be required, upon the form prescribed by the said Employer for the faithful performance and proper fulfilment of the said Contract or in the event of non-withdrawal of the said Bid within the time specified for its validity then this obligation shall be void and of no effect, but otherwise to remain in full force and effect.

PROVIDED THAT the Guarantor shall forthwith pay to the Employer the said sum stated above upon first written demand of the Employer without cavil or argument and without requiring the Employer to prove or to show grounds or reasons for such demand notice of which shall be sent by the Employer by registered post duly addressed to the Guarantor at its address given above.

PROVIDED ALSO THAT the Employer shall be the sole and final judge for deciding whether the Principal has duly performed his obligations to sign the Contract Agreement and to furnish the requisite Performance Security within the time stated above, or has defaulted in fulfilling said requirements and the Guarantor shall pay without objection the sum stated above upon first written demand from the Employer forthwith and without any reference to the Principal or any other person.

IN WITNESS WHEREOF, the above bounden Guarantor has executed the instrument under its seal on the date indicated above, the name and seal of the Guarantor being hereto affixed and these presents duly signed by its undersigned representative pursuant to authority of its governing body.

Guarantor (Bank)

Witness: 					    	Signature

1.  						    	Name

Title

Corporate Secretary (Seal)

2.

(Name, Title & Address)				Corporate Guarantor (Seal)

FORM OF CONTRACT AGREEMENT

THIS CONTRACT AGREEMENT (hereinafter called the “Agreement”) made on the _____ day of _______________(month) 20_____ between _______________________________ _______________________________________________________ (hereafter called the “Employer”) of the one part and _____________________________________ (hereafter called the “Contractor”) of the other part.

WHEREAS the Employer is desirous that certain Works, viz _______________ should be executed by the Contractor and has accepted a Bid by the Contractor for the execution and completion of such Works and the remedying of any defects therein.

NOW this Agreement witness as follows:

- In this Agreement words and expressions shall have the same meanings as are respectively assigned to them in the Conditions of Contract hereinafter referred to.

- The following documents after incorporating addenda, if any except those parts relating to Instructions to Bidders shall be deemed to form and be read and construed as part of this Agreement, viz:

- (a)	The Contract Agreement

- (b)	The Letter of Acceptance

- (c)	The completed Form of Bid

- (d)	The Preamble to Conditions of Contract

- (e)	The Particular Conditions of Contract

- (f)	The General Conditions of Contract

- (g)	The priced Schedule of Prices

- (h)	The completed Schedules to Bid

- (i)	The Specifications

- (j)	The Drawings

3.	In consideration of the payments to be made by the Employer to the Contractor as hereinafter mentioned, the Contractor hereby covenants with the Employer to execute and complete the Works and remedy defects therein in conformity and in all respects with the provisions of the Contract.

4.	The Employer hereby covenants to pay the Contractor, in consideration of the execution and completion of the Works as per provisions of the Contract, the Contract Price or such other sum as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

IN WITNESS WHEREOF the parties hereto have caused this Contract Agreement to be executed on the day, month and year first before written in accordance with their respective laws.

Signature of the Contactor	Signature of the Employer

______________________	_____________________

(Seal)	(Seal)

Signed, Sealed and Delivered in the presence of:

Witness:	Witness:

________________________	__________________________

(Name, Title and Address)	(Name, Title and Address)

FORM OF PERFORMANCE SECURITY

(Bank Guarantee)

Guarantee No._____________________

Executed on _____________________

Expiry date _____________________

[Letter by the Guarantor to the Employer]

Name of Guarantor (Bank) with address:__________________________________________

Name of Principal (Contractor) with address:_______________________________________

___________________________________________________________________________

Penal Sum of Security (express in words and figures)________________________________

___________________________________________________________________________

Letter of Acceptance No. ________________________________Dated ______________

KNOW ALL MEN BY THESE PRESENTS, that in pursuance of the terms of the Bidding Documents and above said Letter of Acceptance (hereinafter called the Documents) and at the request of the said Principal we, the Guarantor above named, are held and firmly bound unto the __________________________________________________ (hereinafter called the Employer) in the penal sum of the amount stated above for the payment of which sum well and truly to be made to the said Employer, we bind ourselves, our heirs, executors, administrators and successors, jointly and severally, firmly by these presents.

THE CONDITION OF THIS OBLIGATION IS SUCH, that whereas the Principal has accepted the Employer's above said Letter of Acceptance for ________ __________________________________ (Name of Contract) for the _______________ 

_______________________________ (Name of Project).

NOW THEREFORE, if the Principal (Contractor) shall well and truly perform and fulfill all the undertakings, covenants, terms and conditions of the said Documents during the original terms of the said Documents and any extensions thereof that may be granted by the Employer, with or without notice to the Guarantor, which notice is, hereby, waived and shall also well and truly perform and fulfill all the undertakings, covenants terms and conditions of the Contract and of any and all modifications of said Documents that may hereafter be made, notice of which modifications to the Guarantor being hereby waived, then, this obligation to be void; otherwise to remain in full force and virtue till all requirements of Clause 30, Defects after Taking Over, of Conditions of Contract are fulfilled.

Our total liability under this Guarantee is limited to the sum stated above and it is a condition of any liability attaching to us under this Guarantee that the claim for payment in writing shall be received by us within the validity period of this Guarantee, failing which we shall be discharged of our liability, if any, under this Guarantee.

We, ____________________________________ (the Guarantor), waiving all objections and defences under the Contract, do hereby irrevocably and independently guarantee to pay to the Employer without delay upon the Employer's first written demand without cavil or arguments and without requiring the Employer to prove or to show grounds or reasons for such demand any sum or sums up to the amount stated above, against the Employer's written declaration that the Principal has refused or failed to perform the obligations under the Contract which payment will be effected by the Guarantor to Employer’s designated Bank & Account Number.

PROVIDED ALSO THAT the Employer shall be the sole and final judge for deciding whether the Principal (Contractor) has duly performed his obligations under the Contract or has defaulted in fulfilling said obligations and the Guarantor shall pay without objection any sum or sums up to the amount stated above upon first written demand from the Employer forthwith and without any reference to the Principal or any other person.

IN WITNESS WHEREOF, the above-bounden Guarantor has executed this Instrument under its seal on the date indicated above, the name and corporate seal of the Guarantor being hereto affixed and these presents duly signed by its undersigned representative, pursuant to authority of its governing body.

_______________

Guarantor (Bank)

Witness:

1. _______________________		   	Signature _______________

_______________________		   	Name __________________

Corporate Secretary (Seal)

Title ___________________

2. _______________________

_______________________			_______________________

Name, Title & Address				 Corporate Guarantor (Seal)

FORM OF BANK GUARANTEE/BOND FOR ADVANCE PAYMENT

Guarantee No.________________

Executed on________________

Expiry date ________________

[Letter by the Guarantor to the Employer]

WHEREAS the _________________________________________________ (hereinafter called the Employer) has entered into a Contract for _____________________________ ________________________________________________________________________ _______________________________________________ (Particulars of Contract), with ___________________________________________________________________ ________________________________ (hereinafter called the Contractor).

AND WHEREAS the Employer has agreed to advance to the Contractor, at the Contractor’s request, an amount of _________________________________ (Rs.___________________) which amount shall be advanced to the Contractor as per provisions of the Contract.

AND WHEREAS the Employer has asked the Contractor to furnish Guarantee to secure advance payment for performance of his obligations under the said Contract.

AND WHEREAS __________________________________________________ (Bank) (hereinafter called the Guarantor) at the request of the Contractor and in consideration of the Employer agreeing to make the above advance to the Contractor, has agreed to furnish the said Guarantee.

NOW THEREFORE the Guarantor hereby guarantees that the Contractor shall use the advance for the purpose of above mentioned Contract and if he fails, and commits default in fulfillment of any of his obligations for which the advance payment is made, the Guarantor shall be liable to the Employer for payment not exceeding the aforementioned amount.

Notice in writing of any default, of which the Employer shall be the sole and final judge, as aforesaid, on the part of the Contractor, shall be given by the Employer to the Guarantor, and on such first written demand payment shall be made by the Guarantor of all sums then due under this Guarantee without any reference to the Contractor and without any objection.

This guarantee shall come into force as soon as the advance payment has been credited to the account of the Contractor.

This guarantee shall expire not later than ______________________________________

by which date we must have received any claims by registered letter, telegram, telex or telefax.

It is understood that you will return this Guarantee to us on expiry or after settlement of the total amount to be claimed hereunder.

_______________

Guarantor (Bank)

Witness:

1. _______________________		   	Signature _______________

_______________________		   	Name __________________

Corporate Secretary (Seal)

Title ___________________

2. _______________________

_______________________			_______________________

Name, Title & Address				 Corporate Guarantor (Seal)

SPECIFICATIONS

SPECIAL PROVISIONS

(To be prepared and incorporated by the Employer)

SPECIFICATIONS - SPECIAL PROVISIONS (Sample Clauses)

SP-1	WORK BY CONTRACTOR

SP-2	WORK BY OTHERS

SP-3	FACILITIES PROVIDED BY THE EMPLOYER

SP-4	DESCRIPTION OF THE PROJECT

SP-5	ACCESS TO SITE

SP-6	SITE CONDITIONS

SP-7	STANDARDS AND DESIGN

SP-8	DRAWINGS AND INFORMATION

SP-9 	INSTRUCTION MANUALS

SP-10 	CONTRACTOR TO COOPERATE WITH OTHERS

SP-11	INSTRUCTIONS AND TRAINING OF EMPLOYER'S STAFF

SP-12	ERECTION AND TESTING EQUIPMENT AND MAINTENANCE TOOLS

SP-13	SPARE PARTS

SP-14	PACKING

SP-15	ERECTION MARKS

SP-16	PROGRAMME

SP-17	PROGRESS REPORTS AND MEETINGS

SP-18	PHOTOGRAPHS

SP-19	SECTIONS OF THE WORKS

SP-20	QUALITY ASSURANCE

SP-21	SUBCONTRACTS

SP-22	INSPECTION AND TESTING

SP-23	TESTS ON COMPLETION

SP-24	TAKING OVER

SP-25 	TRANSPORTATION AND HANDLING OF PLANT

SP-26  	DEFECTS AFTER TAKING OVER

SP-27	DIRECTED AND REQUIRED

SP-28	PAYMENT FOR WORK REQUIRED BY SPECIAL PROVISIONS

SP-29	SAFETY AND HEALTH

SP-30	RATING PLATES, NAMEPLATES AND LABELS

SPECIFICATIONS

TECHNICAL PROVISIONS

(To be prepared and incorporated by the Employer)

[Note for Preparing the Specifications

A set of precise and clear specifications is a prerequisite for bidders to respond realistically and competitively to the requirements of the user without qualifying their Bids. The specifications must be drafted to permit the widest possible competition and, at the same time, present a clear statement of the required standards of workmanship, materials, performance of the works. Only if this is done objectives of economy, efficiency, and fairness in procurement will be realized and responsiveness of Bids can be ensured, and the subsequent task of bid evaluation can be facilitated. The specifications should require that materials to be incorporated in the works be new, unused, and of the most recent or current models, and incorporated all recent improvements in design and materials unless provided for otherwise in the contract.

Samples of specifications from similar previous procurements are useful in this respect. The use of metric units is encouraged. Depending on the complexity of the works and the repetitiveness of the type of procurement, it may be advantageous to standardize the Technical Specifications that should cover all classes of workmanship, materials and equipment although not necessarily to be used in a particular procurement.

Care must be taken in drafting specifications to ensure that they are not restrictive. In the specification of standards for equipment, materials, and workmanship, recognized international standards should be used as much as possible. The specifications shall consider all site conditions but not limited to seismic conditions, weather conditions and environmental impact. The specifications should state that equipment, materials, and workmanship that meet other authoritative standards, and which ensure at least a substantially equal quality than the standards mentioned, will also be acceptable. The following clause may be inserted in the Specifications.

Sample Clause: Equivalency of Standards and Codes

Wherever reference is made in the Specifications to specific standards and codes to be met by Works to be furnished and tested, the provisions of the latest current edition or revision of the relevant shall apply, unless otherwise expressly stated in the Contract. Other authoritative standards that ensure equivalence to the standards and codes specified will be acceptable.]

# SPECIAL PROVISIONS

SP 1	WORK BY CONTRACTOR

  - The present part covers the general specifications for design, manufacture: shop testing, erection, supervision, site test and commissioning of the equipment.

  - The purpose of this section is to provide the bidder and manufacturer with the general technical requirements applicable to the equipment specified in the particular technical specifications are therefore, to be read in connection with the same.

  - The bidder shall examine the specifications of the chapter in close connection with the other documents and particulars form part of the bid and contract documents and all addenda and amendments, if any thereto issued prior to the opening date for bidding. He shall also make him aware to all conditions and aspects which might in any way influence his bid.

  - If the specifications of the bidding documents do not contain particulars of material or works which are obviously necessary for the proper and safe, completion, operation and maintenance of the equipment in question, all such materials and works shall be deemed to be included in the supply.

  - If the bidder finds discrepancies in or omissions from specifications or from other documents or should be in doubt as to their meaning, he shall immediately contact the employer, for interpretation, clarification or correction thereof before submitting his bid. Such actions shall, however in no case be considered as cause for altering opening date of bidding.

SP 2	WORKS BY OTHERS

  - Close cooperation and coordination between the different contractors concerned (mechanical, electrical, civil hydraulic steel works and other shall be observed, so that different items of he works with respect to design, dimension and operation match and complement each other in the very vast and most economical manner.

SP 3	FACILITIES PROVIDED BY THE EMPLOYER

  - The employer will provide at no cost to the contractor, such documents information data prepared by the employer, to enable the contractor, to supply installation, commission and test running of the goods.

  - In consideration of services performed by the contractor under this contract the employer shall make such payments and, in such manner, as in provided by clause of this contract.

  - The employer has no accommodation facility at project site, the contractor shall arrange the accommodation facility to the engineers and technical personals during installation, commissioning and test running of the plant and visit of other technical experts.

SP 4	DESCRIPTION OF THE PROJECT

  - The project site is located at a distance of 155 Km from Chitral Town at Yukum village Yarkhoon Valley District Upper Chitral Khyber Pakhtunkhwa.

SP 5	ACCESS TO SITE

i)	Chitral Yarkhoon road: 			155 Km from Chitral Town.

SP 6	SITE CONDITIONS

Temperature of the sites various from -200c to +400c. During summer the temperature remains very pleasant and severe cold during winter season.

SP 7.1	STANDARDS AND DESIGN

    - Standards adaptable are as under: -

DIN		German standards, issued by the detaches institute for Normung eV

JIS		Japanese Standards Association

ISO		International Organization for Standardization

IEC		International Electro Technical Commission

ASTM		American Society for Testing of Material

AWS		American Welding Society

ASME		American Society of Mechanical Engineers

NFPA		National Fire Protection Association, USA

    - Whichever standard is chosen, it shall be made available in the English languages. The latest revision or edition in effect at the time of the invitation of tenders shall apply.

    - The equipment and materials furnished under this contract shall conform to the requirements of the specifications and to the designated standards.

    - Materials for general purpose shall have a quality equal to, or better than the following (it shall be clearly stated by contractor which standard is applied).

| Cast steel for general engineering purpose | ASTM A 27, Grade 65,35 DIN 1681, GS 45.3 WI .466 |
| --- | --- |
| Iron casting gey | ASTM A 278 Class 35 DIN 1969, GG 25 |
| Iron casting modular | ASTM A 536, DIN 1693, GGG 40 WI 7040 |
| Steel forging for generator rotors | ASTM A 469, class 1 |
| Flanged Joint | DIN subject groups 2810,2820,2850, 2870, 2880 |
| Structural steel general | ASTM A 36, DIN 17100, Rst 37-2 |
| Structural steel weld able fine grained | DIN 17102 DIN 17100 ST 52-3 |
| Bronze Castings | ASTM B 584, Alloy 2B DIN 1716, SnPbBz 10 |
| Bronze for bearing Bushings thrust discs etc. | ASTM B 584, Alloy 3A DIN 1716, SnPbBz 10 |
| Welded and seamless steel piping | ASTM A 53, Grade A DIN 1626, 1628, 1629, 1630 |
| Stainless steel piping | ASTM A 269, Grade type 304L DIN 7440, W 4301 |
| Stainless steel plates | ASTM A 269, Grade type 3041, DIN 17440, WI 4301 |
| Stainless steel casting | ASTM A 487 DIN 17445 |
| Babbitt Metal for bearing | ASTM B 23, Grade 3 DIN 1703p591X |
| Turbine shaft steel | ASTM A 668, Class ID DIN 17200 impact strength |

    - Special requirements are provided in the detail specifications under construction elements in this technical specification.

    - Due consideration shall be made to dynamic stresses, which shall be kept within the stress limits. The effects of corrosion, stress concentrations notches, etc. shall be duly considered.

SP 7.2	DESIGN

# GENERAL

- The purpose of this section is to provide the bidder and manufacturer with the general technical requirement applicable to the equipment specified in the particular technical specifications are therefore to be read in conjunction with the same.

- All equipment supply shall be designed according to modern and accepted engineering practice. All calculations shall be based on accepted methods and standards. All equipment shall be designed duly considering unforeseen loads and stresses, e.g. during transportation erection, etc. likewise, the designer shall duly consider the requirements of easy operation, maintenance and replacement of wormed parts as well as a long life of service under the prevailing site conditions. All information related to the supplies shall be based on the international system of units (SI Units). The design of turbines, generators, Governor etc. of all sites should be done with the consideration that all T/G sets/power station will be run isolated and of grid surge relief valves should be supplied for the units having long penstocks to ensure stability.

7.2.1	NOISE

i.	The noise level caused by the installed operating equipment shall not exceed the following values.

--	Machine hall workshop etc. at any place 1 m distant from operating equipment.

--	Office control room’s etc.					Max 85dB

--	First and room, etc.						Max 55dB

--	Residential areas		Day time			Max 50dB

Night time			Max 35dB

ii.	The noise level definition and measurement shall be in accordance with latest ISO and IEC standards.

iii.	The values stated shall be adhered to taking a normal civil construction into account. Particular of the civil construction shall be submitted by the engineer at the contractor, request. The noise level will be measured at the time of operation of the Hydrogenerator Sets for which arrangement shall be made by the contractor.

7.3.	HYDRAULIC SYSTEM

7.3.1	Oil Pumps

Pumps for hydraulic system shall be of the displacement type parallel to each pump or group of pumps operating in parallel, a relief valve of sufficient capacity to bypass the full delivery of the pumps at a pressure only 10% above the maximum allowable working pressure shall be provided as a safety measure.

7.3.2	Oil Pressure Tanks

Oil pressure tanks shall be of welded construction, designed constructed and tested in accordance with the ASME boiler and pressure vessel code. Section VIII for 1.5 times the maximum system operation pressure.

7.3.3	Sump Tanks

The capacity of the sump tank shall be not less than that required containing all of the oil that can be discharged back into the sump by completely discharging the oil in the system. The oil volume in the sump tank shall be sufficient to maintain the oil level within an adequate working level during operation.

7.3.4	Oil Sump tanks shall provide with:

--	Suitable access openings.

--	Fine mesh strainer combined with a magnetic filter through which all oil retuning from the servomotors shall pass. The strainer shall be readily removable for cleanings.

--	Humidity separating air filter.

--	Flush mounted oil level indicator.

--	Capped filler hole with a suitable strainer.

--	Drain connection with hand operated shut off valve.

Sump tanks must be installed so that the bottom of the tank and the drain connection are a least 400 mm above the floor.

The interior of the tank shall be free of crevices, open joints or dead end holes, and all welds inside the tank shall be continuous. The interior and exterior surfaces shall be cleaned and pained as specified in these general technical specifications.

7.3.5	Hydraulic Oil Piping.

All main piping shall be seamless tubing with welded joints approved couplings or steel flanges for bolted connections. All piping shall be thoroughly cleaned oiled and protected for shipment by protectors on all flanges and plugs on pipe ends. If stainless steel piping is used, no painting is required; such piping requires couplings and fittings of identical materials. All gate valves in the pressure lines shall be of the cast steel solid wedge, rising stem type with close guide clearance to minimize vibration of the gates when operating at partial opening. Piping shall be shop fabricated to the maximum extent possible consists with erection, handling and shipping requirement so as to reduce fieldwork.

7.3.6	Compressed Air Systems.

The provision of safety for compressed air system shall conform with internationally accepted standards.

Vessels shall be of the cylindrical, vertical type, The vessel shall be mounted on a structural steel base. Each vessel shall be equipped with the following provisions:

- Intel sockets with valves.

- Outlet sockets with valves.

- Pressure safety valve.

- Dial pressure gauges, one with four electric contacts.

- Drains valve.

In case the pressure vessel is used for pressurized oil or water systems the vessel shall further be equipped with:

- One (magnetic) level gauge with shut off valves.

- Level indicators with electric contacts in number as required.

Each vessel has to pass a pressure test a 1.5 x nominal pressure lasting for 8 hours in the manufacturer workshop before coating is applied.

Each vessel shall be furnished with a test certificate.

7.3.7	Compressors shall be provided with:

-	Automatic lubrication

-	Air intake filter and silencer

-	Thermometer for measuring temperature of the compressed air.

-	Automatic shut down if the discharge air temperature exceeds a predetermined adjustable valve.

-	Unloading valves

-	Water drain valves

-	Water and oil separator

-	Pressure safety valve

-	Cooler for compressed air

-	Non turn valve

-	Inlet pressure valve

7.3.8	The water and oil separator shall be equipped with an automatic solenoid operated drain valve to achieve automatic draining standstill. Both compressor stages shall be equipped with un-loader valves which shall close time delayed after start to avoid compressor start against full pressure.

7.3.9	The compressor shall be delivered as package units on common frame with the appropriately sized AC squirrel cage motor and the respective motor control center ready for operation.

7.3.10	Cooling System.

An independent affective oil cooling system should incorporate with a mechanism of pumping oil through tail water. The pump should be coupled with the prime mover shaft instead of an electric motor.

7.4	ELECTRIC EQUIPMENT.

7.4.1	Electrical Equipment Materials.

All materials incorporated in the equipment supplied shall be new and 	commercials quality free from defects and imperfections.

Materials for heavy electrical equipment machines or assemblies shall comply with the requirements stated under the relevant sections of general specification, for mechanical equipment. Copper used as electrical conductors shall be of the electrolytic type and comply with respective ASTM or DIN standard.

    - Standardization of Equipment.

The contractor shall endeavor to standardize all small and mechanical and electrical equipment materials and devices for the work, he shall arrange and perform the necessary co-ordination work with his subcontractors for the purpose of such standardization. Such equipment’s devices fittings etc, shall comprise but not necessarily be restricted to the following:

- Valves gauges, flow meters, thermometers, etc.

- Electrical instruments and meters

- Terminals and terminal blocks.

- Auxiliary relays.

- Contractors, fuses, miniature breakers.

- Control devices and switches.

- Lamp, bulbs, sockets, plugs etc.

- Lubricants.

7.4.3 Surface treatment and painting Electrical Equipment.

The electrical machinery and equipment shall be treated as stated under the general specification for mechanical equipment. Control boards, panel boards, cubical, cabinets etc. in dry room shall have interior surfaces painted with at least one priming and one finishing coat of anti-corrosion paint. Exterior surfaces shall be adequately treated to be substantially corrosion resistant with prime coat, one filler coat and two finishing coats. Other indoor installation. In dry room shall be carefully cleaned, if possible sand blasted and painted with two coats of oil resistant paint. Outdoor fittings for distribution boxes etc. shall be hot dip galvanized minimum film of zinc 600g/m2

Other outdoor and indoor installations in wet and damp rooms shall be hot dip galvanized if possible, wherever galvanizing is not possible at least two coats of paint on zinc power basis shall be applied after cleaning. In general, all equipment shall be adequately be treated for tropical condition.

The supplier’s standard procedure for surface treatment may accepted if it is equivalent to or better than stated above.

The color codes for cables pipe work etc. shall adopted as per international practice.

  - Design and construction

7.5.1	General Requirements.

The works shall be designed for reliable and safe operation under all conditions. Facilities shall be available to simplify inspection, testing, maintenance and repair of the works. The design shall also include all necessary provisions ensuring the safety of the operation maintenance personnel.

All electrical equipment, apparatus and devices shall be of suitable design for satisfactory operation under the climate conditions prevailing at the site. The equipment shall also operate satisfactorily under normal load and voltage variations as well as during abnormal conditions to be expected during services, provided that these remain within the assigned ratings of the apparatus.

All electrical connections and contacts shall be of ample cross section and capacity for carrying continuously the specified current without undue heating and shall be secured by bolts or set screws of ample size fitted with lock washers of approved types.

All out door apparatus including bushing, insulators and fittings shall be designed so that water cannot collect at any point.

All exposed bearings shall be designed with water traps, so that water cannot creep along the shaft into the apparatus housing.

Cubicles cabinets and similar enclosed compartments containing electrical equipment shall specially treat on the exterior and interior surfaces to prevent corrosion and be adequately ventilated. All major or important compartments containing electrical equipment shall be provided with internal lightening facilities. Anti- condensation heaters shall be installed where required.

All interior surfaces of electrical apparatus, cabinets, etc. including contact’s relays, coils, etc. shall be treated in an approved manner to prevent mold growth. Such treatment shall in no way interfere with the proper operation of the equipment either electrically or mechanically. All cabinets shall be vermin proof with screened openings. Outdoor cabinets shall be dust proof with screened openings. Outdoor cabinets shall be dust proof. All cables shall vermin proof.

Porcelain used for bushings, insulators and the like shall be sound free from defects and thoroughly vitrified. Insulation shall not depend on the porcelain glaze. The porcelain shall be of the wet process fabrication, brown glazed pattern.

Bigger assemblies such as switch boards etc shall be designed to enable suitable to enable suitable transportation of sub-assemblies.

Whenever any of the maximum of 24 hours average temperatures exceed the normal service conditions temperatures of the IEC recommendations for the relevant equipment.

For cables in the ground 30c shall be taken as design value for ambient (ground) temperature.

7.5.2	Switch Boards and panels.

I.V. switch boards and control relay and metering boards panels shall be of robust construction formed of a steel frame and covered with smooth steel plate. The steel plate shall be at least 2.5 mm thick and properly stiffened to prevent distortion. Whenever required hinged steel doors with latches shall be provided, doors shall be lockable by means of approved key locks.

Boards and panels shall be designed constructed and tested in accordance with IEC publication No. 439 factory-built assemblies of low voltage switch gear and control gear. Boards and panels shall be totally enclosed and the degree of protection according IEC publication No. 144/529 shall be:

- Indoor minimum IP 32

- Outdoor IP minimum IP 54

The frames of the boards shall be designed to permit firm anchoring on the floor or on the panel pedestal for the purpose as part of the concrete floor construction. The frames shall permit easy erection, and allowance shall be made for extension of the board by similar additional panels.

The contractors supply shall include all necessary-mounting brackets framing foundation bolts and respective embedded metal to permit proper installation of the boards.

Unless otherwise specified or agreed upon all instrument apparatus and devices on the panel fronts shall be provided for flush mounting.

7.5.3	Wiring and Terminal Blocks.

All wiring shall be stranded conductor, PVC insulated with equivalent insulation suitable for operation at the rated voltages and current with adequate safety factor compliance with provisions of the applicable IEC recommendations.

For wiring within boards, the “bunch” patterns shall adopt. For a small number of connections, wiring may be grouped using flexible plastic bands or equivalent. For a large number of connections, a system using support strips or U-shaped troughs (with covers) shall use. The latter principle arrangement shall apply for cable distribution racks. All wiring shall be clearly marked and identified.

All wiring shall terminate at terminal blocks. The latter shall be of the molded type and provided with barriers to separate power circuits from control circuits. It shall be appropriate, terminal blocks shall be equipped with facilities for testing, such as short circuiting, separating.

Terminal blocks for different voltages shall not be mixed between on another. The blocks shall group for each voltage and they shall be clearly marked for easy identification of the system voltage.

Terminal blocks using screws action directly on the wire (conductor) as well as spring type terminal blocks are not acceptable. To avoid squeezing of the wire the screw pressure shall applied by a pressure plate having smooth edges.

For current transformer circuits and voltage transformer circuits only one conductor shall be connected to each side of a terminal block and the brand off shall be made by interconnection the necessary number of neighboring blocks by means of copper strips.

For other circuits no more than two conductors shall be allowed to be connected to each side of a terminal block.

The wiring identification shall be by numbered ferrules sleeves or other approved means. To avoid opening of current transformer circuits by mistake the terminal blocks for such circuits shall clearly marks.

All cables control wiring and terminals shall be marked in a systematic manner, both on the drawings and on the cables, wires and terminals themselves. The markings shall be in accordance with a system presented and co-ordinate by the contractor throughout the works.

All wiring ends shall be marked in such a way as to identify both the point of connection and particulars wiring source.

7.5.4	CABLE LAYING AND ROUTING:

The final routing of HV and LV cables in indoor and outdoor installations shall be determined by the contractor from the directives given in this section. All cable routing and arrangement shall subject to the engineer approval.

For indoor installations and exposed outdoor installations cables shall be laid in covered cable trenches, plastic or steel ducts or depending on the available space on cable trays and racks. Where few and small cables have to be laid they can be fixed directly to the wall or ceiling cables have to be laid they can be fixed directly to the wall or ceiling cables on wall shall be protected against mechanical damage at least up to 18 m above the floor.

Low power cable i.e. cables for control metering etc. shall not be run in close parallel to high power cables or earth wires but shall be run at the greatest possible separating distance. Additionally, cables for extra low power i.e. mA and mV circuits and cables connected to low power solid state electronic circuits shall be screened and otherwise protected against disturbance as required.

LV cables in the switchyard shall be laid in covered concrete cable trenches with which shall be laid in conduits.

The cable trenches including trench covers shall be furnished or provided by the civil works contractor, Ducts, conduits and cable racks for the same shall never the less be furnished by the contractor.

For multiphase cable laid in trenches no fixing materials are necessary. In all other cases the necessary materials and equipment for laying fixing etc, of the cables shall be provide by the contractor.

Note Required cable up to step up Transformer shall be provided by the contractor

7.5.5	ELECTRIC MOTORS.

For all electric power drivers, 03 phase squirrel cage type induction motors shall be used. All motors shall be of the totally enclosed type (IP54 or better according to IEC publication 34.5). Winding insulation shall class F throughout.

Starting shall be direct on line. All motors shall be so designed that start up may be affected successfully at 85% of the rated voltage of the motor.

All motors shall have overload and short circuit protection.

Ratings and dimensions shall be in accordance with the relevant IEC publications.

All motors including all auxiliary and protective device, shall be capable of running continuously with full load at voltages raking between 85% and 110% of the rated supply voltage.

Special attention shall be paid when designing the electric motors on account of the temporary frequency rises and falls which may be applied to the motor terminals.

7.5.6	SWITCHES AND FUSES:

Automatic power switching shall be done by contractors. Contractors as par to be internal electrical system to apparatus shall preferably be the same make as used in the auxiliary power supply system.

Fuse links shall be provided by miniature circuit breakers of the same make as in the auxiliary power supply system. However, glass tube fuses may be use for protecting small power electronics circuits.

  - ELECTRIC MOTORS.

7.6.	ELECTRIC MOTOR

# EQUIPMENT SPECIFICATION

The turbine will be of horizontal type with the runner mounted directly on to generator shaft. All the parts / component of the turbines will be designed keeping in view the fact that water driving the units contains sand and silt particle. The minimum overall efficiency of the turbine will conform to the international standard and shall not be less than 92% turbine shall be designed according to international standard s and it will be free of cavitation. The turbine shall be designed for solvated off grid operation, penstock of most of the sites, are extra ordinary long, therefore surge relief valve shall be made part of the unit to ensure stability at the time load variation and load application / rejection.

7.6.1	RUNNER

The runner shall be casted in monadic in stainless steel 13:4 Cr Ni.

The water surfaces will be carefully machined and polished to a smooth surface and controlled by templates to ensure uniform shape.

7.6.2	GUIDE VANES

The guide vanes shall be machined from stainless steel 13:4 Cr Ni.

7.6.3	SPIRAL CASING

The casing shall be either casted or welded from steel plates of sufficient thickness

. The casing will be primed to protect it from rusting.

The casing must be provided with: -

- Hand hole for inspection

- Lifting eye bolts.

7.6.4	CONTROL SYSTEM / GOVERNING

The turbine will be equipped with a complete best quality speed control governor acting on the guide vanes for the sudden load rejection and application. The turbine will be designed for manually and automatically controlled operations for the single/ parallel operation with provision for black start. The PID governor PLC connected with PC. The Manual operation shall be through a wheel for direct control of guide vanes.

The control system will be comprising of hydraulic speed governor with hydraulic speed governor hydraulic amplifier /power pack, distribution valve and servo motor linked guide vane mechanism. Governing mechanism along with hydraulic power amplifier distribution valve and servomotor shall be manufactured by reputed manufacturer with auxiliary equipment such as synchronizer motor and solenoid shutdown etc. there should be provision of compressed air or gas connections to facilitate black start of the turbo generator.

7.6.5	PIPE AND BOLTS

All oil pipes shall be stainless steel or galvanized pipe.

All water and air pipe shall be of stainless steel.

All bolts in contact with water shall be stainless steel.

7.6.6	INLET VALVE

The inlet valve shall be butterfly type for Francis turbine made of a reputed manufacturer. Limit switches including percentage opening shall be provided in addition to open and close. There should be provision manual as well as motorized.

7.6.7	INLET CONE

Transmission pieces between penstock and valve (inlet cone) shall be included in supply facilities for drawing of penstock pip shall be provided with inlet cone in the form of a pipe and valve between the inlet valve and tailrace.

7.6.8	FLEXIBLE FLANGED ADAPTOR

Flexible flanged adaptor should be provided between inlet valve and inlet pipe

  - FRANCIS TURBINE

# EQUIPMENT SPECIFICATION

The turbine will be horizontal shaft type with the runner directly mounted onto generator shaft. The minimum overall efficiency of the turbine will conform to international standards and shall not be less than 92%. The turbine shall be designed according to international standard and it shall be cavitation free.

The turbine parts/components shall be of the following specification. All turbine parts shall be designed keeping in view that the water driving the units contains both silt and sand.

# 7.7.1.	SPIRAL CASING

The spiral casting consists of a stay ring and plate shell fully welded from fine gained steel. The stay rings consist of an upper and lower disc and the stay welded in between the discs. The spiral casing is designed to withstand and tested at hydraulic pressures of 1.5 times the static pressure. The case is stress relieved and is designed to ensure that the water flow reaches the turbine runner at correct angel with a minimum of hydraulic losses.

The spiral casing must be provided with

- Air relief at the highest point on the volute.

- Hand hole for inspection

- Connections/nipples for the pressure measurement.

- Connection for drainage.

- Lifting eye bolts

# 7.7.2	GUIDE VANES

Material:	Rust free stainless steel 13:4 Cr Ni

The guide vanes are cast integral with their spindle/shaft, grinded polished and machined. The guide vanes are supported by self-lubricating bushed. Each guide vane will be supported by means of a carefully calibrated ring feeder coupling. The guide vane operating levers will be linked together and their positions will be controlled by the governor servomotors.

# 7.7.3.	TURBINE COVER

Both upper and lower covers shall be machined and filled with replaceable seal rings made of nickel aluminum bronze.

# 7.7.4.	RUNNER

Material:	Rust free stainless steel 13:4 Cr Ni

The runner will be cast integral in monobloc. The runner will be stress relieved by heat treatment if required. The runner shall be machined grinded and polished. It shall be balanced to ensure noise and vibration free operations. The number will be directly mounted onto the generator shaft by shrunk fir with oil pressure.

# 7.7.5.	DRAFT TUBE

The draft tube will consist of a conical section made of mild steel, a 90 bend and a draft tube cone made of mild steel plates. The draft tube will be equipped with manometer for observation of draft tube vacuumed/pressure.

# 7.7.6	CONTROL SYSTEM

The control system shall comprise of a best quality PID hydraulic speed governor of PLC type with hydraulic power amplifier, distribution valve and servomotor linked to the master guide vane lever for automatic operation. The upper cover must be equipped with grease lubricated bronze bushes for regulating guide vane shaft. There should be provision of compressed air or gas for the facility of black start of the turbo generator.

  - GENERAL SPECIFICATION OF ELECTRIC EQUIPMENTS

Design production, rating characteristic, test etc. of all electrical equipment shall strictly comply with the IEC, and other international standards. The intention of the section is not specifying the supply in detail but to give guidelines to the manufacturers to obtain an optimal design for the particular application. The equipment shall be simple and robust, easy to repair locally as far as possible: -

    - GENERATOR

- The generator offered shall be of well-proven construction preferably selected from the manufactures existing range for similar climatic conditions.

- The generator shall be of robust design made of high-quality materials and shall be as far as possible maintenance free.

- The excitation system shall be of the brushless type.

- The generator and excitation system shall be designed for operating safely and stably under the conditions mentioned in these documents.

- The generator and bearing shall be able to withstand transient and continuous runway speed without any consequential damages.

Each unit shall be a three-phase synchronous generator to which a horizontal turbine shall be coupled on the free end. The generator shall be supplied with suitable set of bearings which shall absorb loads and forces from both turbine generator and flywheel. Flywheel on the non-drive end to be installed for the required inertia of the rotating part shall be supplied with the generators. The flywheel shall be mounted onto the rotor shaft shrunk fir through oil pressure.

- The alternator shall be horizontal shaft 03 phase 4 wire synchronous type with enclosed circulating ventilation having air or other suitable method of cooling, composed of stator, rotor, exciter, rotation rectifiers, varistor, suitable designed bearings, common base frame, temperature sensor etc.

- The stator shall consist of frame, core and coil etc. The core shall be so designed to withstand extremely high temperatures due to any untoward incidents. The winding of stator shall be made of best quality copper. The generator reactance shall be kept as low as possible to minimize voltage drop and ensure stable operation.

- The rotor is composed of main shaft, magnetic yoke, poles and fan etc. The main shaft is made of forged steel. The yoke is shrunken on the main shaft to form and integral part.

- The pole consists of pole core and field coils etc. The pole core shall be laminated with 16 Mn steel plate and field coil is made of flat copper wires. The generator rotating parts, shall be supported on well-designed bearings.

- Temperature detectors (Pt-100 DN or equivalent) i.e. minimum three (03) in the stator winding. 3 in the cores and one in each of the bearing shall be installed. And condensation heaters in the stator shall be provided as per site conditions given in specific work data (Schedule A to instruction to tendered)

- Speed monitoring device for RPM indication and over speed protection shall be provided. The device shall also send signals to the controlling equipment for shut down of Hydrogenator Set.

- The stating, stopping, synchronizing, load and voltage control or the unit shall be auto operated controlled/besides manual controlled from the panels. The governor and the main valve, shall also be equipped with automatic tripping and stopping facilities in case emergency.

The control panel shall be equipped with the following instruments protection relays and equipment.

7.9.2.	INSTRUMENTS.

-	KW meter (Digital)

-	Volt Meter (Digital)

-	Frequency Meter

-	Power Factor Meter

-	RPM Meter

-	KVAR Meter

-	Hour Volt Meter

-	DC Volt Meter

-	Thermometers (Digital)

-	Forebay Water Level Indicator Including Float Switch.

-	Synchronous scope with double volt meter, double frequency meter including lamps.

7.9.3.	PROTECTION RELAYS

-	Over Current

-	Short Circuit

-	Over/under voltage

-	Over/under frequency

-	Reverse power relay

-	Differential protection (3 phases)

-	De-excitation

-	Earth fault

-	Thermistor

-	synchronization check relay

7.9.4.	EQUIPMENT

-	Low voltage air circuit breaker for the unit

-	Automatic voltage regulator (AVR) with accessories

-	Isolator for the unit

-	Batteries and charges for DC Supply based on designer discretion

-	Fault indicating digital monitor with the unit.

# SP 8	DRAWINGS AND INFORMATION

    - The drawing (Map of NA is attached) and other information will be provided to the bidder/contractor on written request. However, the supplier will furnish the following drawings and information during the commissioning to hydro generating sets.

  - Instruction book spare parts catalogue, maintenance drawings.

  - Operating and maintenance manuals shall be supplied by the contractor/supplier for the equipment furnished by him in English language.

  - All instruction manuals must contain the following information: -

-	Detailed description.	Included herein will be a complete detailed description of the equipment its sub-assemblies, components and accessories. A detailed list of clearances, tolerances, temperatures, settings, etc. is required.

-	Principles of operations.	A brief summary is required of the technical basis for operation of the equipment including line diagrams, wiring diagrams, piping diagrams and the like.

-	 Operating instructions.	The instructions must be clear and concise, and preferably in sequence of operation.

-	Testing and adjustment.	The complete procedure of testing and adjusting the system or equipment during operation, after overhaul or during recommended periodic check must be covered.

-	Maintenance instruction.	This will be divided into two subsections.

i)	Preventive maintenance. Which will indicate the periodic inspections required, the inspection procedure the routing cleaning and lubricating procedures the routine safety checks and the like.

ii)	Repair and adjustment which will spares are to be provided under the contract documents, troubleshooting guide, electrical, fluid or mechanical circuit tracing repair and adjustment procedures.

  - Spare parts catalogues shall be supplied giving all necessary data of ordering spare parts directly from the manufactures.

  - Detailed maintenance drawings shall be supplied in view of enabling the employer’s maintenance staff to carry out proper maintenance and repair work. These drawings shall indicate sufficient details, dimensions, quality and specification of materials utilized and whatever necessary assembly clearances, to enable the manufacture in the employer’s workshop of such parts as it is common practice to do.

  - When such instruction books have been prepared for a major components or system, the contractor shall submit three draft copies of the book to the employers for his approval.

  - After the approval has been received and all necessary changes made the contractor shall deliver five (5) bound copies of the book to the employer.

SP 9	INSTRUCTION MANUALS:

  - Instruction book spare parts catalogues, maintenance drawings.

  - Operating and maintenance manuals shall be supplied by the contract/supplier for the equipment furnished by him in English language.

  - All instruction manuals must contain the following information: -

- Detail Description

- Principal of operation

- Testing and adjustment procedure

- Maintenance Instruction

  - Spare parts catalogues shall be supplied giving all necessary data for ordering spare parts directly from the manufacturers.

  - Detailed maintenance drawing shall be supplied in view on enabling the employer’s maintenance staff to carry out proper maintenance and repair work. These drawings shall indicate sufficient details, dimensions, quality and specification of materials utilized and whatever necessary assembly clearances, to enable the manufacture in the employer’s workshop of such parts as it is common practice to do.

  - When such instruction books have been prepared for a major component or system, the contractor shall submit three draft copies of the book to the employer for his approval.

  - After the approval has been received all necessary changes made the contractor shall deliver five (5) bound copies of each instruction book to the employer.

SP 10	CONTRACTOR TO COOPERATE WITH OTHER

Close cooperation and coordination with the members of Silgan development organization and other officials of AKRSP.

SP 11	INSTRUCTION AND TRAINING OF EMPLOYER’S STAFF

The contractor shall arrange free visit/training of employer’s engineers at the manufacture’s works as followings:

  - Two Engineers of E&M trade will visit Ex-factory to finalized designed parameter as at contractor expenses 03 weeks before start of manufacturing process.

  - Two Engineers of E&M trade during manufacturing and inspection of machinery / equipment and manufactures works the inspect process the design and manufacturing for two weeks.

  - On job training at site 6 staff during installation/commissioning, operation and test running of the plant. The boarding and lodging of such trainees will be arranged by the community.

SP 12	ERECTION AND TESTING EQUIPMENT AND MAINTENANCE TOOLS PER SITE

The contractor shall provide equipment for erection and testing of hydro generator sets at site and shall provide following maintenance tools.

SP-14		PACKING

14.1	After shop assembly, inspection and testing all parts of the works shall be carefully packed and marked so as to ensure ready erection at the site in the correct respective locations.

14.2	Each package, box and crate shall be waterproof clearly marked with identification for the project weigh (net and gross), dimensions special instructions for slinging package number etc. marks shall be brand marked or stenciled with good quality waterproof ink or paint so as to be clearly visible.

14.3	All costs involved with packing and temporary storage and transport of all items shall be included in the tender price.

14.4	One copy of each packing list shall be enclosed with the shipment it shall be suitably protected against humidity and damage.

14.5	The works shall be manufactured and packed in conformity with the loading limitations and gauges for the chosen routing from the manufacturer country to the site. The contractor shall be responsible for respecting all such transport limitations.

14.6.	The packing list shall include final weights and dimensions of particularly heavy goods, such as turbine components, valves, steel liners, generator parts. Local storage at site will be provided by the employer. In case of special or heavy equipment the contractor shall submit packing and transport plans for the engineer’s study and approval at a reasonable time prior to packing. Transportation of heavy goods for turbine and valve shall arrive at site at such time that it may be unloaded by the powerhouse main crane as directed by the engineer.

14.7	All packing shall be seaworthy for under deck storage or on deck storage as required.

SP-15		ERECTION MARKS

15.1	All permanent equipment of the works shall be provided with securely fastened nameplate showing the markers name, model, serial number, year of manufacture, main characteristic data of the respective equipment and further relevant information specified in the applicable standards necessary for proper identification of the equipment involved. All main equipment shall have the nameplate in English.

15.2	The contractor shall supply all label plates and other labeling (of the screw or tape) on control boards, control desks, panels and other places where required for operational, functional and safety reasons. The labeling size of the plates and their locations shall be subject to approval by the engineer. A sample label plate (with indication of the material used) with lettering shall be submitted for this purpose. The number of sizes of the various plates shall be kept to a minimum. All labeling shall be in the English languages.

SP-16		PROGRAMME

The contractor shall provide the programme in written form to supplier for further clarification.

16.1	The contractor shall submit to the engineer for his approval the program which shall contain the following:

a)	The order in which the contractor proposes to carry out the works (including design, manufacture, delivery to site, erection, testing and commissioning).

b)	The time when submission and approval of the contractor’s drawing are required.

c)	The times by which the contractors require the employer:

i)	To furnish any employer’s drawings.

ii)	To provide access to the site.

iii)	To have completed the necessary civil engineering work (including foundations for the plants and)

- To have obtained any import licenses consents, way leaves and approval necessary for the purpose of the works.

16.3	The contractor shall submit the program in the form stated in the preamble within 28 days after the commencement date.

The approval by the engineers of the program shall not relieve the contractor or the employer from any obligation under the contract.

SP-17		PROGRESS REPORTS AND MEETINGS

The contractor shall provide progress report and written request may be submitted to the employer for meetings to clarify any curries if any.

SP-18		PHOTOGRAPHS

The contractor shall provide all necessary drawing and photographs before commissioning of Hydrogenator Sets. However, except with the prior written authorization to the employers the contractor shall not exhibit or permit to be exhibited any photographs or advertisement on the works. Any authorization exhibition shall be immediately removed if the employer so requires.

SP-19		SECTIONS OF THE WORKS

The detail of section of the works is given in the schedule A to this document.

SP-20		QUALITY ASSURANCE

The contractor shall ensure the quality as per international standard.

SP-21		SUB CONTRACTOR

Not Applicable

SP-22		INSPECTION AND TESTING

The Engineers from AKRSP will inspect the design, manufacturing and testing of the equipment at the manufacturer works. The expenses including air ticket from Pakistan to the manufacturer’s country, boarding lodging, training and local transportation etc.

SP-23		TEST ON COMPLETION

The contractor should arrange testing equipment’s and technical manpower to carryout necessary tests after commissioning of the Hydrogenator set.

SP-24		TAKING OVER

A taking over certificate will be issued to the contractor by the employer after taking necessary tests for satisfactory functioning of the equipment.

SP-25		TRANSPORTATION AND HANDLING OF PLANT

The contractor should be responsible for safe transportation and handling for the plant from manufacturers works to site of erection and shall procure and submit in insurance cover to the employer.

SP-26		DEFECTS AFTER TAKING OVER

26.1	If any part the work is taken over separately from the works the defects liability period to that part shall commence on the date it was taken over.

26.2.	the contractor shall be responsible for any defect in or damages to any part pf the work which may appear or occur during the defects liability period and which arises from either.

a) 	any defective materials, workmanship or design or

b)	any act or omission of the contractor during the Defect Liability Period.

The contractor shall make good the defects or damages as soon as practicable and at his own cost.

SP-27		DIRECTIVES AND CLARIFICATION

Engr Zeeshan will be coordinator for clarification and directives.

SP-28		PAYMENT FOR WORK REQUIRED BY SPECIAL PROVISIONS

No additional payment will made for the works mentioned in the special provision.

SP-29		SAFETY AND HEALTH

The contractor shall maintain such records and make such reports concerning safety, health and welfare of persons and damages to property as the Engineer may from to time prescribe.

SP-30		RATING PLATES, NAMEPLATES AND LABELS

The nameplates, rating plates and labels particularly for turbine valves, generator, governor, panel boards should clearly be affixed.

Delivery schedule

| S.NO | Name of HPP | No. of unit | Capacity | Delivery Schedule |
| --- | --- | --- | --- | --- |
| 01 | 1x230 KW Dizg HPP at Yukum, Yarkhoon Upper Chitral | 01 | 1x230 KW | 6 Months from Ex-factory to port of Entry at Pakistan 03 Months for Carriage, installation & commissioning and test running |

The delivery schedule shall be effective from the date of the singing of the contract/agreement

EVALUATION CRITERIA

MANUFACTURER’s AUTHORIZATION

As the Turbine-Generator sets are not manufactured in the country, the bidder shall provide the manufacturer’s authorization showing that the bidder has been duly authorized by the manufacturer of the plant and equipment to supply and install that item in the employer’s project site. Failure to submit the manufacturer’s authorization at the first instant lead to rejection being non-responsive.

Manufacture’s authorization:

To

Insert complete name of Employer)

Whereas

We (Insert complete name of manufacturer) who are official manufacturer of Turbine-Generator sets in having Factories at (Insert full address of manufacturer’ factory) do hereby authorized (Insert complete name of the bidder) to submit a bid the purpose of which is to provide the required plant / equipment manufactured by us and to subsequently to sign the contract.

We hereby extend our full guarantee in accordance with the specification stipulated in the bidding documents.

Signed:	(Insert signature of authorized representative of the manufacturer)

Name:	(Insert complete name of representative) duly authorized to sign this authorization on behalf of (Insert complete name of manufacturer)

Dated on ------------day of ------------- 2025

EVALUATION CRITERIA

- The Technical Proposals will be evaluated prior to opening Financial Proposals. The evaluation shall be carried out based on documentary evidence provided by the Bidder in support of their technical capability and compliance with the specified requirements.

The evaluation will be carried out using a scoring system with a total of 100 marks, of which the minimum qualifying score shall be 70 marks. Only bidders obtaining 70 or more marks shall be considered technically qualified and Bidders must achieve a minimum of 50% of the allocated marks in each category for qualifying to open the financial bids.

The evaluation shall be based on a weighted scoring system, where:

- Technical Proposal: 70% weightage

- Financial Proposal: 30% weightage

- After verifying responsiveness, the lowest evaluated bid will be awarded maximum financial marks (100), and others will be scored using the following formula:

- Financial Score (Fs)=(Lowest Evaluated Bid PriceBidder’s Evaluated Bid Price)×100

- The Combined Score (CS) for overall evaluation will be computed as:

- CS=(0.70×Technical Score)+(0.30×Financial Score)

|  | CATEGORY | WEIGHTAGE/MARKS |
| --- | --- | --- |
| 1 | Experience record | 35 |
| 2 | Personnel capabilities | 15 |
| 3 | Quality of goods and equipment capability, Operation, Maintenance & Training Capability | 20 |
| 4 | Financial Capabilities | 30 |

- Credit marks shall be awarded on the basis of following qualification:

  - General Experience

Client references/testimonials/Workorder/Completion Certificate Must be submitted, only submitting list will not be considered.

| Sr# | Description | Maximum points |
| --- | --- | --- |
| 1 | Over all Experience: Experience in the role of contractor, sub-contractor for at least 5 years prior to the submission of the bid. With equivalent bid amounts at least five projects. One Mark per project. | 5 |
| 2 | Similar nature of projects and complexity. Experience in role of contractor and completed installation, commissioning and test running of at least three T/G sets in the last ten years having capacity of 250KW and above with completion certificates. At least two T-G sets should be imported. 3 Marks per project | 15 |
|  | Supply and installation of at least one T/G sets in hand and completed more than 60% work. 5 Marks per project | 10 |
| 4 | Status of enlistment with Government organization s and other agencies | 5 |
|  | SUB_TOTAL | 35 |

2.2 Personnel Capabilities:

| Sr# | Description | Maximum Points |
| --- | --- | --- |
| 1 | Graduate Engineers (Electrical/Mechanical) 2 marks for per person (a)Number of Engineers (b) Experience of Engineers in number of years | 6 3 |
| 2 | Number of Diploma Engineers in Employment of the firm (a)Number of Engineers (b) Experience of Engineers in number of years | 4 2 |
|  | SUB_TOTAL | 15 |

2.3 Quality of goods and services

| Sr# | Criteria for Quality of goods and services | Maximum Marks |
| --- | --- | --- |
| 1 | Quality of Product with certification | 05 |
| 2 | Delivery Lead Times | 05 |
| 3 | After Sales Service (Experience in O&M of small hydropower plants (at least 2 projects) | 05 |
| 4 | Required Equipment List (Lift, alignment tool, welding etc.) | 05 |
|  | SUB-TOTAL | 20 |

2.4 Financial Capabilities:

| Sr# | Description | Maximum Marks |
| --- | --- | --- |
| 1 | Available Bank line credit | 5 |
| 2 | Working capital in last three years | 10 |
| 3 | Litigation History (if nil) | 5 |
| 4 | Black listing from any agency if not black listed | 5 |
| 5 | Valid License to execute Electro mechanical work | 5 |
|  | SUB- TOTAL | 30 |

The evaluation shall be carried out as follows:

JOIN VENTURES

Joint ventures must comply with the following requirements.

1.The lead partner shall meet not less than 40% of share.

2. Each of the partners shall meet not less than 25% of share.

3. The joint venture partners must collectively satisfy the criteria.

4.A change in JV after qualification shall be subject to approval of employer.

Bid shall be signed by all the partners.

| 2 | Working capital in last three years | Full mark will be given if the average working capital is more than 60.00 million If less than 60.00 million use the formula 5x(A/60.00) |  |
| --- | --- | --- | --- |
| 3 | Black listing from any agency if not black listed | In case the bidder is black listed from any agency, no marks will be given and full marks will be given in case affidavit by the bidder attached. |  |
| 4 | Valid License to execute Electro mechanical work | No point will be given if license is not attached to execute the electro mechanical work. |  |
| 5 | Litigation History (if nill) | In case the bidder is involve in any litigation no marks will be given and full marks will be given in case of affidavit by the bidder attached for no litigation |  |