### PREQUALIFICATION NOTICE

Aga Khan Rural Support Program

Prequalification of HDPE Pipe Manufacturers and Authorized Distributors

Issue Date:  July 16, 2026
Closing Date: July 31st, 2026
Reference Number: AKRSP/PQ/HDPE//2026-0

### 1. INTRODUCTION AND BACKGROUND

1.1 Invitation for Prequalification

The Aga Khan Rural Support Programme (AKRSP) is a not-for-profit organization registered under section 42 of the Companies Ordinance 1984. It works to improve the livelihoods of people living in the Gilgit-Baltistan and Chitral. AKRSP works in the fields of social organization, institutional development, resource development, natural resource management, infrastructure development, entrepreneurship, and market development.

The objective is to empanel a shortlist of qualified and approved suppliers for the procurement of high-quality High-Density Polyethylene (HDPE) pipes and fittings for its projects. This initiative aims to ensure the provision of safe and sustainable potable water to the communities in the Gilgit Baltistan, Chitral and Sind.

1.2 Project Objective

The primary objective of this prequalification notice is to establish a pre-qualified list of competent and reliable HDPE pipe manufacturers and suppliers. This shortlist will then be invited to participate in a transparent and competitive bidding process for the supply of materials. This two-stage process ensures that only vendors who meet the stringent technical, financial, and ethical criteria set by AKRSP and Donors  are considered for   projects.

1.3 Scope of the Prequalification Process

This process is intended to:

- Identify manufacturers and authorized suppliers/Distributors with the requisite technical capability, production capacity, and financial standing.

- Ensure compliance with national and international quality standards for HDPE pipes and fittings.

- Shortlist qualified vendors for the subsequent tendering stage.

- Facilitate a fair, transparent, and efficient procurement process in accordance with the best practices of development organizations.

1.4 Validity of Prequalification

Prequalification documents submitted by applicants must remain valid for a period of 90 days from the closing date of submission. The prequalification status, once granted, will be valid for the for a period as approved and decided by Aga Khan Rural Support Program

1.5 Right to Accept or Reject

AKRSP reserves the right to withdraw from this prequalification process at any stage or to accept or reject any or all applications without assigning any reason. Any decision made by AKRSP in this regard shall be final and binding.

### 2. INSTRUCTIONS TO APPLICANTS

2.1 Eligible Applicants

Applications are invited from:

- Original Manufacturers: HDPE pipe manufacturers who own and operate a manufacturing facility.

- Authorized Distributors/Suppliers: Entities that are officially authorized by an original manufacturer to supply HDPE pipes. Such applicants must provide a valid and current authorization certificate from the manufacturer.

2.2 One Application Per Entity

Each manufacturer or distributor may submit only one application. If a manufacturer submits an application in its own name, it cannot also be an authorized distributor for another applicant in this process.

2.3 Cost of Application

All costs and expenses associated with the preparation and submission of the application shall be borne by the applicant. AKRSP will not be responsible for any such costs, regardless of the outcome of the prequalification process.

2.4 Clarifications

Prospective applicants may request clarifications regarding this prequalification document. All requests for clarification must be submitted in writing via email or letter to the address provided in Section 12 of this document, no later than 14 days before the submission deadline. AKRSP will respond to all valid queries in writing and may circulate the responses to all applicants, without disclosing the source of the query.

2.5 Amendment of Prequalification Document

At any time prior to the submission deadline, AKRSP may, for any reason, amend this prequalification document. The amendment will be communicated to all applicants who have expressed interest, and it will be binding on them. To allow applicants reasonable time to consider the amendment, AKRSP may, at its discretion, extend the submission deadline.

2.6 Language

All documents and correspondence related to this prequalification shall be in the English language.

2.7 Joint Ventures (JV)

A joint venture between two or more firms is eligible to apply, provided they meet the required criteria collectively. In the case of a JV, a notarized Memorandum of Understanding (MoU) on stamp paper, outlining the roles, responsibilities, and share of work of each partner, must be submitted. The lead partner must be clearly designated.

2.8 Conflict of Interest

Applicants must ensure they do not have any conflict of interest aand AKRSP conflict of interest policy. Any applicant found to have a conflict of interest will be disqualified.

### 3. LEGAL & REGULATORY COMPLIANCE

Applicants must provide documented proof of the following to be considered responsive. Non-compliance with any of these mandatory requirements will result in immediate disqualification.

| Requirement | Details |
| --- | --- |
| Company Registration | Must be a registered company in Pakistan with a valid National Tax Number (NTN) and Sales Tax Registration (GST). The applicant must be an Active Taxpayer with the Federal Board of Revenue (FBR) and provide proof of the same (e.g., Active Taxpayer Certificate).Pakistan Engineering Council registration should be attached with documents. |
| Manufacturer's Authorization (for Distributors/Suppliers) | If applying as an Authorized Distributor/Supplier, a comprehensive and official authorization certificate from the HDPE pipe manufacturer must be provided. This certificate must clearly specify the product range, validity period, and territories covered. |
| Supporting Letter from Manufacturer | A supporting letter from the manufacturer detailing the complete specifications, raw materials used (including source and grade), and quality control processes for the pipes is mandatory. This letter must be on the manufacturer's official letterhead and signed by an authorized officer. |
| PSQCA Standards Compliance | Compliance with Pakistan Standards & Quality Control Authority (PSQCA) applicable standards for HDPE pipes is mandatory. A valid PSQCA license or a certificate of conformity to PSQCA standards (or equivalent international standards) must be submitted. |
| Non-Blacklisting Declaration | The applicant must provide a signed and stamped undertaking on original stamp paper declaring that the firm is not blacklisted by any government agency, donor, or financial institution in Pakistan or any other country. The declaration must also confirm that the firm is not involved in any litigation that could materially affect its ability to perform the contract. |

### 4. TECHNICAL SPECIFICATIONS & PRODUCT REQUIREMENTS (MANDATORY)

This is a core section of the prequalification criteria. Vendors must confirm their unequivocal ability to supply HDPE pipes and fittings that meet the following stringent technical specifications. Non-compliance with any of the mandatory technical requirements will result in disqualification.

4.1 Raw Material Requirements

- Material Grade: The pipes must be manufactured from PE-100 grade raw material. PE-100 is a high-performance polyethylene that allows a Minimum Required Strength (MRS) of 10 MPa, providing superior long-term strength and resistance to environmental stress cracking.

- Minimum Induced Wall Stress: The pipe must be designed to allow a minimum induced wall stress of 5 N/mm² at 27°C (80°F), consistent with the PE-100 design criteria.

- Approved Resin Suppliers: The resin (raw material) must be sourced exclusively from internationally recognized, approved suppliers to ensure quality and consistency. Approved resin suppliers include, but are not limited to: Borealis, Borouge, LyondellBasell, Prime Polymer, Sabic, SCG, Sinopec, Tasnee, IRPC, BP Rigidex, Petronas, Solvay, Phillips 66, Fina, Dow, and DuPont Novocan.

- Quality of Material: The raw material must be exclusively virgin material. The use of recycled or reworked material is strictly prohibited. The material must contain only the necessary and approved additives, such as:

  - Antioxidants: To prevent degradation during processing and service life.

  - UV Stabilizers: To protect against the harmful effects of ultraviolet radiation from sunlight.

  - Carbon Black: To provide UV protection and uniform color. The carbon black content must be within the range of 2% to 3% by weight.

- Density: The density of the PE-100 material must be ≥ 0.945 g/cm³.

4.2 Standards Compliance

All HDPE pipes and fittings supplied under this scheme shall fully comply with the following international standards:

- ISO 4427 : Plastics piping systems - Polyethylene (PE) pipes and fittings for water supply.

- DIN 8074: Polyethylene (PE) pipes - Dimensions.

- DIN 8075: Polyethylene (PE) pipes - General quality requirements, testing.

- DIN 16963: Pipe joint assemblies and fittings for high-density polyethylene (PE-HD) pressure pipes.

- DIN 16776: Fittings of polyethylene for pipelines with spigot and socket.

- DIN 19533: Pipes and fittings of polyethylene for sewers and drains.

Equivalent international standards that provide the same or higher level of quality and performance may be accepted, subject to the prior written approval of AKRSP Engineers. The applicant must provide proof of equivalence.

4.3 Pipe Specifications

- Pressure Rating (PN): Pipes and fittings shall be designed for a nominal working pressure as specified below. The pipes must be suitable for potable water use.

  - PN 10: For all pipes sizes 20mm to 360 mm and above if applicable.

  - PN 16: For all pipes sizes 20mm to 360mm (for high-pressure zones).

  - PN 20: For all pipes sizes 20mm to 360mm (for high-pressure zones).

- Standard Dimension Ratio (SDR): The SDR is directly related to the PN. The following SDRs are required for PE-100 material:

  - PN 10: SDR 17

  - PN 16: SDR 11

  - PN 20: SDR 9

- Color and Marking:

  - The pipes must be black in color with a blue stripe running along their length for easy identification as potable water pipes.

  - Pipes shall be clearly and indelibly marked by the manufacturer along their length. The marking must include:

    - Manufacturer's name or trademark.

    - Nominal diameter (e.g., DN 110).

    - Pressure rating (e.g., PN 16).

    - Material grade (e.g., PE 100).

    - Standard(s) complied with (e.g., ISO 4427 / DIN 8074).

    - Batch number/Production code.

- Packing:

  - Pipes (up to 90mm diameter) shall be supplied in coils of a minimum 100 meters length to minimize joints and above 20 feet length pipe.

  - Both ends of the pipes must be sealed with suitable caps to prevent the ingress of dirt, dust, or moisture during transit and storage.

  - Pipes must be protected against UV exposure, rain, and mechanical damage through appropriate packaging and handling.

4.4 Fittings Requirements

- Fittings Material: Fittings may be manufactured from HDPE, Polypropylene (PP), or engineering plastics. All fittings must be compatible with the pressure rating (PN 10, PN 16, PN 20) and pipe specifications.

- Fittings Standards: All fittings shall comply with the relevant DIN and ISO standards, including DIN 16963, DIN 19533, and ISO 4427.

- Fittings Types: The following types of fittings are acceptable for the scheme:

  - Butt Fusion Fittings: Used for creating permanent, high-strength joints using butt fusion welding.

  - Electrofusion Fittings: Used for creating secure joints using electrofusion sleeves.

  - Compression Fittings: Used for quick and easy connections, particularly for smaller diameters and in situations where fusion welding is impractical. These fittings must have O-ring sealing to prevent leaks.

- Pressure Rating: Fittings must be designed for the same pressure rating as the pipes they are connecting to.

### 5. TESTING & QUALITY ASSURANCE

The HDPE pipes must be manufactured and tested under a stringent Quality Assurance (QA) and Quality Control (QC) program.

5.1 Mandatory Factory Tests

- Acceptance Test: This test must be conducted for each batch (defined as a maximum of 2 km of pipe length). The test is conducted at 20°C (68°F) for 1 hour, according to DIN 8075. The pipe must withstand the internal pressure without leakage or rupture.

- Quality Test: This test is mandatory and must be conducted at least once a month for each production line. The test is conducted at an elevated temperature for 170 hours, according to DIN 8075. The pipe must show ductile failure behavior (i.e., no brittle cracking) and must not leak or rupture.

5.2 Material Tests

- Melt Flow Rate (MFR) Test: To verify the material's flow properties and ensure it is within the specified range for PE-100.

- Density Test: To confirm the density of the material is ≥ 0.945 g/cm³.

- Carbon Black Content/Dispersion Test: To verify the correct percentage and uniform dispersion of carbon black.

5.3 Third-Party Certification

- Product Certificates: The manufacturer must provide valid third-party test certificates from a reputable and internationally accredited laboratory verifying that the pipes and fittings comply with the required standards (ISO, DIN, etc.).

- Material Certificate: The manufacturer must provide a certificate from the resin supplier confirming the quality and grade (PE-100) of the raw material, including the batch number and date of supply.

- Approved Third-Party Certificate: The Contractor shall provide an approved third-party certificate to verify the chemical constituents of the material, confirming compliance with the specifications for potable water use.

### 6. PRODUCTION & SUPPLY CAPACITY

Applicants must demonstrate sufficient production and supply capacity to meet the project's requirements.

| Requirement | Details |
| --- | --- |
| Production Capacity | The manufacturer must have an annual production capacity sufficient to meet the total project within the required delivery schedule. Evidence of production capacity, such as a list of extrusion lines and their capacities, must be provided. |
| Stock Capacity | The applicant must maintain adequate stock of all system components (pipes and fittings) to meet ongoing market and project demand. |
| Delivery Capacity | The vendor must be able to complete delivery within a maximum period of 30 days from the date of the order to commence. The vendor must provide a delivery schedule outlining the logistics plan. |

### 7. LOGISTICAL CAPACITY & GEOGRAPHIC PRESENCE

7.1 Logistical Capacity

The vendor must demonstrate a robust logistical capacity to deliver pipes and fittings to the designated storage sites in the challenging terrain of Gilgit-Baltistan and Chitral. This includes:

- Transportation: The vendor must have access to appropriate vehicles (e.g., flatbed trucks, trailers) capable of safely transporting HDPE pipes over long distances and mountainous roads.

- Handling and Storage: The vendor must provide a detailed plan for handling and protecting the pipes during transit and storage to prevent any damage.

- Delivery Plan: A comprehensive delivery schedule and plan must be submitted, outlining the phased delivery of materials.

### 8. ORGANIZATIONAL CAPACITY & EXPERIENCE

8.1 Proven Experience

- Minimum 5 Years: The applicant must have a minimum of 5 years of proven experience in the manufacturing and/or supply of HDPE pipes for large-scale water supply projects in Pakistan.

- Similar Projects: Must provide at least three (3) references of completed projects of a similar scale and nature (supply of HDPE pipes for water supply schemes, preferably in the public sector or with international development organizations like NGOs, AKDN, or government departments). Each reference must be supported by a work order and a completion certificate.

8.2 Technical Workforce

The applicant must maintain a dedicated, trained, and certified technical workforce.

| Requirement | Details |
| --- | --- |
| Key Personnel | Must have a dedicated point of contact for the project. Provide CVs of key technical personnel, including production managers, quality control engineers, and logistics managers. |
| Installation Support Staff | While the scope is primarily supply, the vendor may be required to provide technical support or training for jointing and installation. The applicant must demonstrate the availability of skilled technicians (e.g., certified butt fusion/electrofusion welders). |

8.3 Past Performance

- The applicant must have good standing in the local market with a history of successful project deliveries.

- Experience in partnering with development sector organizations (e.g., NGOs, AKDN, government departments, donors) will be given preference.

### 9. FINANCIAL REQUIREMENTS

Applicants must demonstrate sound financial health to handle a contract of this magnitude.

| Requirement | Details |
| --- | --- |
| Financial Stability | Provide audited financial statements and bank statements for the last 3 years (2023, 2024, 2025). |
| Average Turnover | The average annual turnover must be sufficient to handle a huge contract . This will be verified from the audited financial statements and income tax returns. A minimum average annual turnover of PKR 200 Million is required for manufacturing companies. |
| Net Worth & Working Capital | The applicant must demonstrate a positive net worth and adequate working capital (Current Assets - Current Liabilities) to manage the project's cash flow requirements. |
| Performance Bond | Upon winning the tender, the successful bidder must provide a Performance Bond of 10% of the contract value from a scheduled bank. |
| Advance Payment Guarantee | If a mobilization/advance payment (up to 20% of the contract value) is requested, the vendor must provide a corresponding Advance Payment Bond/Guarantee from a scheduled bank. |

### 10. WARRANTY, AFTER-SALES & GENERAL REQUIREMENTS

| Service | Commitment |
| --- | --- |
| Warranty/Guarantee | The bidder must agree to a Period of Maintenance of 12 months from the date of completion (i.e., from the date of delivery and acceptance). The warranty period for the pipes should be a minimum of 15 years. |
| Protection & Packing | Ensure all pipes are adequately protected against damage for the entire period of transit and storage, suitable for up to three years. |
| Handling | Pipes shall be transported and handled using methods that prevent damage (e.g., lifting beams, canvas slings). |
| Inspection | The vendor must allow the Purchaser/Engineer to inspect goods at any time. Materials will only be accepted upon passing inspection at the storage site. |
| Supply of Apparatus | The Contractor shall supply appropriate pipe jointing and cutting apparatus. |
| Manuals | The Contractor shall supply manuals (in English) for the joining of PE pipes. |

### 11. PARTNERSHIP COMMITMENT WITH AKRSP

- Willingness to Partner: The applicant must be willing to work  in partnership with AKRSP.

- Adherence to Quality Assurance: The applicant must be willing to abide by AKRSP quality assurance and verification processes.

- Joint Monitoring: The applicant must agree to joint monitoring, reporting, and compliance protocols.

- Training and Collaboration: The applicant must be willing to participate in training or awareness sessions organized by AKRSP.

### 12. ETHICAL & SOCIAL COMPLIANCE

- Environmental and Social Safeguards: The applicant must comply with AKRSP environmental and social safeguards, including the AKDN's Environmental and Social Framework (ESF).

- Non-Blacklisting: The applicant must not be blacklisted by any government agency, donor, or financial institution.

- Ethical Business Practices: The applicant must adhere to strict ethical business practices and demonstrate corporate social responsibility.

- Undertaking: The applicant must provide an undertaking on original stamp paper for non-blacklisting, non-litigation, and non-refrainment from court.

### 13. SUBMISSION REQUIREMENTS

Applications must be submitted in a sealed envelope and must include the following documents in the order listed below. Any missing document may be grounds for disqualification.

- Organizational Profile: Complete company profile, legal structure, registered office addresses, and a list of key management personnel.

- Legal Registration: Valid NTN and GST registration certificates (Active Taxpayer status proof with FBR) and PEC Certificate updated.

- Authorized Dealership (if applicable): Official authorization certificate from the HDPE pipe manufacturer.

- Product Certifications: Data sheets, test certificates, and certification documents for all products (ISO, DIN, etc.), including the supporting letter from the manufacturer.

- Raw Material Details: Raw material certificate, name of raw material manufacturer, batch number of raw material, and proof of purchase from approved resin suppliers.

- Experience (Similar Work): Details and certificates of completed HDPE pipe supply projects (minimum 3 references). Attach work orders and completion certificates.

- Present Commitments: Details of current contracts or works in hand.

- Key Personnel: Details of key technical and management personnel, including CVs.

- Financial Status: Audited financial statements, tax returns, and bank statements for the last 3 years (2023, 2024, 2025).

- Tax Status: Tax Registration Number and tax paid details for the last 3 years.

- Procurement Proof: Valid proof of purchase of HDPE raw materials in the last three years (sales tax invoices).

- Litigations: Information on any past or pending litigations.

- Blacklisting Declaration: Declaration of non-blacklisting and non-litigation.

- Manufacturing Capacity: Details of manufacturing facilities, including a list of machinery (extrusion lines) and their capacities.

- Any Other Information: Any other information helpful in the prequalification process.

### 14. EVALUATION CRITERIA AND SCORING

AKRSP will evaluate vendors against the following criteria. The minimum passing score is 70%.

| Criteria | Weightage | Details |
| --- | --- | --- |
| Legal & Certification Compliance (Pass/Fail) | Pass/Fail | Mandatory requirements must be met. Non-compliance results in disqualification. |
| Technical Specifications & Product Quality | 25% | Compliance with all technical specifications, standards (ISO, DIN), raw material requirements, and testing protocols. |
| Experience & Past Performance | 20% | Assessment of relevant experience, number and scale of similar projects, and performance record. |
| Financial Capacity | 15% | Evaluation of audited financials, turnover, net worth, working capital, and ability to provide performance bonds. |
| Stock, Logistics & Delivery Capacity | 20% | Assessment of production capacity, ability to meet delivery schedules within 30 days, and a robust logistics plan. |
| Warranty & After-Sales Service | 10% | Willingness to provide the required warranty. |
| Total | 100% | Minimum Passing Score: 70% |

### 15. IMPORTANT NOTES

- Submission Deadline: Applications must be submitted in hard form in a sealed envelope, clearly marked "PREQUALIFICATION - HDPE PIPE ", to the address below by July 31, 2026], before 2:30 PM (PST).

- Address for Submission:

Manager Procurement
Aga Khan Rural Support Program 
Core Office Babar Road Kashroot 
Gilgit.

- Late Submission: Late, incomplete, or emailed documents will not be entertained.

- Validity: Prequalification documents must remain valid for a period of 90 days from the closing date.

- Right to Accept/Reject: AKRSP reserves the right to withdraw from this process at any stage or to accept/reject any or all applications without assigning any reason.

- Accuracy of Information: AKRSP reserves the right to verify all submitted information and may reject applications containing false or misleading information. A site visit to the manufacturing facility may be conducted.

### 16. CONTACT FOR QUERIES

For any queries or clarifications regarding this prequalification notice, please contact:

Manager Procurement
Aga Khan Rural Support Program
Core Office Babar Road Kashroot Gilgit
📞 Phone: 05811-452480

### ANNEXURE A: DETAILED TECHNICAL SPECIFICATIONS FOR HDPE PIPES AND FITTINGS

This annexure provides a comprehensive breakdown of the technical specifications for all HDPE pipes and fittings.

Note: All dimensions are in accordance with ISO 4427 / DIN 8074.

A1. Fittings Specifications

- Elbows (90° and 45°): For directional changes.

- Tees (Equal and Reducing): For creating branch connections.

- Reducers (Concentric and Eccentric): For connecting pipes of different diameters.

- Flanges: For making connections to valves, pumps, and other flanged equipment.

- End Caps: For sealing the ends of pipelines.

- Couplers (Socket Fusion and Electrofusion): For joining pipes of the same diameter.

- Saddles: For tapping into existing mains.

A2. Jointing Methods

- Butt Fusion: The most common and reliable method for joining HDPE pipes. It involves heating the ends of two pipes and pressing them together to form a permanent, leak-proof joint.

- Electrofusion: An advanced method that uses electrically heated coils embedded in a fitting. The fitting is placed over the pipe ends, and an electric current is passed through the coils to melt the plastic and create a fused joint. This is ideal for repairs and tight spaces.

- Compression Fittings: A mechanical jointing method that uses a compression nut and ring to create a seal. This is suitable for temporary installations or where fusion welding is not possible.

A3. Testing Requirements Summary

| Test Type | Test Standard | Condition | Acceptance Criteria |
| --- | --- | --- | --- |
| Acceptance Test | DIN 8075 / ISO 4427 | 20°C for 1 hour | No leak, no rupture |
| Quality Test | DIN 8075 / ISO 4427 | Elevated Temp. (80°C) for 170 hours | Ductile failure, no leak or rupture |
| MFR Test | ISO 1133 | 190°C / 5 kg | Within specified range |
| Density Test | ISO 1183 | 23°C | ≥ 0.945 g/cm³ |
| Carbon Black Content | ISO 6964 | - | 2% - 3% by weight |

A4. Pipe Classification

The following table outlines the minimum wall thickness requirements for PE100 pipes in accordance with ISO 4427 / DIN 8074 . SDR values are calculated based on the formula SDR = (Outside Diameter) / (Minimum Wall Thickness).

| Nominal Diameter (DN) | PN 10 (SDR 17) | PN 16 (SDR 11) | PN 20 (SDR 9) |
| --- | --- | --- | --- |
|  | Outer Dia. (mm) | Min. Wall Thickness (mm) | Outer Dia. (mm) | Min. Wall Thickness (mm) | Outer Dia. (mm) | Min. Wall Thickness (mm) |
| 20 | 20 | 2.0 | 20 | 2.3 | 20 | 3.0 |
| 25 | 25 | 2.3 | 25 | 3.0 | 25 | 3.5 |
| 32 | 32 | 3.0 | 32 | 3.6 | 32 | 4.4 |
| 40 | 40 | 3.7 | 40 | 4.5 | 40 | 5.5 |
| 50 | 50 | 4.6 | 50 | 5.6 | 50 | 6.9 |
| 63 | 63 | 5.8 | 63 | 7.1 | 63 | 8.6 |
| 75 | 75 | 6.8 | 75 | 8.4 | 75 | 10.3 |
| 90 | 90 | 8.2 | 90 | 10.1 | 90 | 12.3 |
| 110 | 110 | 10.0 | 110 | 12.3 | 110 | 15.1 |
| 125 | 125 | 11.4 | 125 | 14.0 | 125 | - |
| 140 | 140 | 12.7 | 140 | 15.7 | 140 | - |
| 160 | 160 | 14.6 | 160 | 17.9 | 160 | 21.9 |
| 180 | 180 | 16.4 | 180 | 20.1 | 180 | 24.6 |
| 200 | 200 | 18.2 | 200 | 22.4 | 200 | 27.4 |
| 225 | 225 | 20.5 | 225 | 25.2 | 225 | - |
| 250 | 250 | 22.7 | 250 | 27.9 | 250 | - |
| 280 | 280 | 25.4 | 280 | 31.3 | 280 | - |
| 315 | 315 | 28.6 | 315 | 35.2 | 315 | - |
| 355 | 355 | 32.2 | 355 | 39.7 | 355 | - |
| 400 | 400 | 36.4 | 400 | 44.7 | 400 | - |

### ANNEXURE B: CHECKLIST OF SUBMISSION REQUIREMENTS

This checklist should be used by applicants to ensure a complete submission.

| Sr. No. | Document | Attached (Yes/No) |
| --- | --- | --- |
| 1 | Organizational Profile & Company Profile | ☐ |
| 2 | Legal Registration (NTN, GST, Active Taxpayer Status) | ☐ |
| 3 | Manufacturer's Authorization (if distributor) | ☐ |
| 4 | Supporting Letter from Manufacturer | ☐ |
| 5 | Product Certifications (ISO, DIN, etc.) | ☐ |
| 6 | Raw Material Certificate & Details | ☐ |
| 7 | Proof of Experience (3 references with work orders & completion certificates) | ☐ |
| 8 | Details of Present Commitments | ☐ |
| 9 | CVs of Key Personnel | ☐ |
| 10 | Audited Financial Statements & Bank Statements (last 3 years) | ☐ |
| 11 | Tax Registration and Tax Paid Details | ☐ |
| 12 | Procurement Proof (Sales Tax Invoices) | ☐ |
| 13 | Litigations Information | ☐ |
| 14 | Blacklisting Declaration | ☐ |
| 15 | Manufacturing Facility Details & Machinery List | ☐ |
| 16 | Joint Venture Agreement (if applicable) | ☐ |
| 17 | Any Other Information | ☐ |